## PVS100
State | Description | Factor | Register | Data Type | Remark
"not use" | Amps | 1 | 40072 | USHORT
"not use" | Amps PhaseA | 0.1 | 40073 | USHORT
"not use" | Amps PhaseB | 0.1 | 40074 | USHORT
"not use" | Amps PhaseC | 0.1 | 40075 | USHORT
"not use" | A_SF | 1 | 40076 | USHORT
"not use" | Phase Voltage AB | 0.1 | 40077 | USHORT
"not use" | Phase Voltage BC | 0.1 | 40078 | USHORT
"not use" | Phase Voltage CA | 0.1 | 40079 | USHORT
"not use" | Phase Voltage AN | 0.1 | 40080 | USHORT
"not use" | Phase Voltage BN | 0.1 | 40081 | USHORT
"not use" | Phase Voltage CN | 0.1 | 40082 | USHORT
"not use" | V_SF | 1 | 40083 | USHORT
"use" | Watts | 0.01 | 40084 | SHORT
"not use" | W_SF | 1 | 40085 | SHORT
"not use" | Hz | 0.01 | 40086 | USHORT
"not use" | Hz_SF | 1 | 40087 | USHORT
"not use" | VA | 0.01 | 40088 | SHORT
"not use" | VA_SF | 1 | 40089 | SHORT
"not use" | Var | 0.01 | 40090 | SHORT
"not use" | VAr_SF | 1 | 40091 | SHORT
"not use" | PF | 0.0001 | 40092 | SHORT
"not use" | PF_SF | 1 | 40093 | SHORT
"not use" | WattHours | 0.01 | 40094 | SW_INT
"not use" | WH_SF | 1 | 40096 | USHORT
"not use" | DC Amps | 0.1 | 40097 | USHORT
"not use" | DCA_SF | 1 | 40098 | USHORT
"not use" | DC Voltage | 0.1 | 40099 | USHORT
"not use" | DCV_SF | 1 | 40100 | USHORT
"not use" | DC Watts | 0.01 | 40101 | SHORT
"not use" | DCW_SF | 1 | 40102 | SHORT
"not use" | Cabinet Temperature | 0.1 | 40103 | SHORT
"not use" | Heat Sink Temperature | 0.1 | 40104 | SHORT
"not use" | Transformer Temperature | 0.1 | 40105 | SHORT
"not use" | Other Temperature | 0.1 | 40106 | SHORT
"not use" | Tmp_SF | 1 | 40107 | SHORT
"use" | Operating State | 1 | 40108 | USHORT | 1: Off 2: Sleeping 3: Starting 4: Normal 5: Throttled(Derating) 6: Shutdown 7: Fault 8: Standby
"not use" | ActWh | 1 | 40187 | FLOAT
"not use" | DC Current_1 | 0.1 | 41123 | USHORT
"not use" | DC Voltage_1 | 0.1 | 41124 | USHORT
"not use" | DC Power_1 | 0.01 | 41125 | USHORT
"not use" | DC Current_2 | 0.1 | 41143 | USHORT
"not use" | DC Voltage_2 | 0.1 | 41144 | USHORT
"not use" | DC Power_2 | 0.01 | 41145 | USHORT
"not use" | DC Current_3 | 0.1 | 41163 | USHORT
"not use" | DC Voltage_3 | 0.1 | 41164 | USHORT
"not use" | DC Power_3 | 0.01 | 41165 | USHORT
"not use" | DC Current_4 | 0.1 | 41183 | USHORT
"not use" | DC Voltage_4 | 0.1 | 41184 | USHORT
"not use" | DC Power_4 | 0.01 | 41185 | USHORT
"not use" | DC Current_5 | 0.1 | 41203 | USHORT
"not use" | DC Voltage_5 | 0.1 | 41204 | USHORT
"not use" | DC Power_5 | 0.01 | 41205 | USHORT
"not use" | DC Current_6 | 0.1 | 41223 | USHORT
"not use" | DC Voltage_6 | 0.1 | 41224 | USHORT
"not use" | DC Power_6 | 0.01 | 41225 | USHORT
"not use" | String Input Current_1 | 0.1 | 41257 | SHORT
"not use" | String Input Current_2 | 0.1 | 41265 | SHORT
"not use" | String Input Current_3 | 0.1 | 41273 | SHORT
"not use" | String Input Current_4 | 0.1 | 41281 | SHORT
"not use" | String Input Current_5 | 0.1 | 41289 | SHORT
"not use" | String Input Current_6 | 0.1 | 41297 | SHORT
"not use" | String Input Current_7 | 0.1 | 41305 | SHORT
"not use" | String Input Current_8 | 0.1 | 41313 | SHORT
"not use" | String Input Current_9 | 0.1 | 41321 | SHORT
"not use" | String Input Current_10 | 0.1 | 41329 | SHORT
"not use" | String Input Current_11 | 0.1 | 41337 | SHORT
"not use" | String Input Current_12 | 0.1 | 41345 | SHORT
"not use" | String Input Current_13 | 0.1 | 41353 | SHORT
"not use" | String Input Current_14 | 0.1 | 41361 | SHORT
"not use" | String Input Current_15 | 0.1 | 41369 | SHORT
"not use" | String Input Current_16 | 0.1 | 41377 | SHORT
"not use" | String Input Current_17 | 0.1 | 41385 | SHORT
"not use" | String Input Current_18 | 0.1 | 41393 | SHORT
"not use" | String Input Current_19 | 0.1 | 41401 | SHORT
"not use" | String Input Current_20 | 0.1 | 41409 | SHORT
"not use" | String Input Current_21 | 0.1 | 41417 | SHORT
"not use" | String Input Current_22 | 0.1 | 41425 | SHORT
"not use" | String Input Current_23 | 0.1 | 41433 | SHORT
"not use" | String Input Current_24 | 0.1 | 41441 | SHORT
"not use" | EVENT_1 | 1 | 40110 | LONG
"use" | %Command Watt Limit | 0.1 | 40233 | USHORT

## PVS50
State | Description | Factor | Register | Data Type | Remark
"not use" | Amps | 1 | 40072 | USHORT
"not use" | Amps PhaseA | 0.1 | 40073 | USHORT
"not use" | Amps PhaseB | 0.1 | 40074 | USHORT
"not use" | Amps PhaseC | 0.1 | 40075 | USHORT
"not use" | A_SF | 1 | 40076 | USHORT
"not use" | Phase Voltage AB | 0.1 | 40077 | USHORT
"not use" | Phase Voltage BC | 0.1 | 40078 | USHORT
"not use" | Phase Voltage CA | 0.1 | 40079 | USHORT
"not use" | Phase Voltage AN | 0.1 | 40080 | USHORT
"not use" | Phase Voltage BN | 0.1 | 40081 | USHORT
"not use" | Phase Voltage CN | 0.1 | 40082 | USHORT
"not use" | V_SF | 1 | 40083 | USHORT
"use" | Watts | 0.01 | 40084 | SHORT
"not use" | W_SF | 1 | 40085 | SHORT
"not use" | Hz | 0.01 | 40086 | USHORT
"not use" | Hz_SF | 1 | 40087 | USHORT
"not use" | VA | 0.01 | 40088 | SHORT
"not use" | VA_SF | 1 | 40089 | SHORT
"not use" | Var | 0.01 | 40090 | SHORT
"not use" | VAr_SF | 1 | 40091 | SHORT
"not use" | PF | 0.0001 | 40092 | SHORT
"not use" | PF_SF | 1 | 40093 | SHORT
"not use" | WattHours | 0.01 | 40094 | SW_INT
"not use" | WH_SF | 1 | 40096 | USHORT
"not use" | DC Amps | 0.1 | 40097 | USHORT
"not use" | DCA_SF | 1 | 40098 | USHORT
"not use" | DC Voltage | 0.1 | 40099 | USHORT
"not use" | DCV_SF | 1 | 40100 | USHORT
"not use" | DC Watts | 0.01 | 40101 | SHORT
"not use" | DCW_SF | 1 | 40102 | SHORT
"not use" | Cabinet Temperature | 0.1 | 40103 | SHORT
"not use" | Heat Sink Temperature | 0.1 | 40104 | SHORT
"not use" | Transformer Temperature | 0.1 | 40105 | SHORT
"not use" | Other Temperature | 0.1 | 40106 | SHORT
"not use" | Tmp_SF | 1 | 40107 | SHORT
"use" | Operating State | 1 | 40108 | USHORT | 1: Off 2: Sleeping 3: Starting 4: Normal 5: Throttled(Derating) 6: Shutdown 7: Fault 8: Standby
"not use" | ActWh | 1 | 40187 | FLOAT
"not use" | DC Current_1 | 0.1 | 41123 | USHORT
"not use" | DC Voltage_1 | 0.1 | 41124 | USHORT
"not use" | DC Power_1 | 0.01 | 41125 | USHORT
"not use" | DC Current_2 | 0.1 | 41143 | USHORT
"not use" | DC Voltage_2 | 0.1 | 41144 | USHORT
"not use" | DC Power_2 | 0.01 | 41145 | USHORT
"not use" | DC Current_3 | 0.1 | 41163 | USHORT
"not use" | DC Voltage_3 | 0.1 | 41164 | USHORT
"not use" | DC Power_3 | 0.01 | 41165 | USHORT
"not use" | EVENT_1 | 1 | 40110 | LONG
"use" | %Command Watt Limit | 0.1 | 40233 | USHORT

## SUN2000
State | Description | Factor | Register | Data Type | Remark
"use" | Active power | 0.001 | 32080 | SW_INT
"not use" | Active power adjustment | 1 | 40196 | SHORT
"not use" | Cabinet temperature | 0.1 | 32087 | SHORT
"not use" | Collect DSP data | 1 | 32002 | SHORT
"use" | Device status | 1 | 32089 | SHORT | 0x0000 Standby: initializing 0x0001 Standby: detecting insulation resistance 0x0002 Standby: detecting irradiation 0x0003 Standby: Grid detecting 0x0100 Starting 0x0200 On-grid 0x0201 Grid connection: power limited 0x0202 Grid connection: selfderating 0x0300 Shutdown: fault 0x0301 Shutdown: command 0x0302 Shutdown: OVGR 0x0303 Shutdown: communication disconnected 0x0304 Shutdown: power limited 0x0306 Shutdown: DC switches disconnected 0xA000 Standby: no irradiation
"use" | Energy yield of current day | 0.01 | 32114 | SW_UINT
"not use" | Grid frequency | 0.01 | 32085 | SHORT
"not use" | Input power | 0.001 | 32064 | SW_INT
"not use" | Locking | 1 | 40699 | SHORT
"not use" | Phase A current | 0.001 | 32072 | SW_INT
"not use" | Phase A voltage | 0.1 | 32069 | SHORT
"not use" | Phase B current | 0.001 | 32074 | SW_INT
"not use" | Phase B voltage | 0.1 | 32070 | SHORT
"not use" | Phase C current | 0.001 | 32076 | SW_INT
"not use" | Phase C voltage | 0.1 | 32071 | SHORT
"not use" | Power factor | 0.001 | 32084 | SHORT
"not use" | PV1 voltage | 0.1 | 32016 | SHORT
"not use" | PV1 current | 0.01 | 32017 | SHORT
"not use" | PV2 voltage | 0.1 | 32018 | SHORT
"not use" | PV2 current | 0.01 | 32019 | SHORT
"not use" | PV3 voltage | 0.1 | 32020 | SHORT
"not use" | PV3 current | 0.01 | 32021 | SHORT
"not use" | PV4 voltage | 0.1 | 32022 | SHORT
"not use" | PV4 current | 0.01 | 32023 | SHORT
"not use" | PV5 voltage | 0.1 | 32024 | SHORT
"not use" | PV5 current | 0.01 | 32025 | SHORT
"not use" | PV6 voltage | 0.1 | 32026 | SHORT
"not use" | PV6 current | 0.01 | 32027 | SHORT
"not use" | PV7 voltage | 0.1 | 32028 | SHORT
"not use" | PV7 current | 0.01 | 32029 | SHORT
"not use" | PV8 voltage | 0.1 | 32030 | SHORT
"not use" | PV8 current | 0.01 | 32031 | SHORT
"not use" | PV9 voltage | 0.1 | 32032 | SHORT
"not use" | PV9 current | 0.01 | 32033 | SHORT
"not use" | PV10 voltage | 0.1 | 32034 | SHORT
"not use" | PV10 current | 0.01 | 32035 | SHORT
"not use" | PV11 voltage | 0.1 | 32036 | SHORT
"not use" | PV11 current | 0.01 | 32037 | SHORT
"not use" | PV12 voltage | 0.1 | 32038 | SHORT
"not use" | PV12 current | 0.01 | 32039 | SHORT
"not use" | PV13 voltage | 0.1 | 32040 | SHORT
"not use" | PV13 current | 0.01 | 32041 | SHORT
"not use" | PV14 voltage | 0.1 | 32042 | SHORT
"not use" | PV14 current | 0.01 | 32043 | SHORT
"not use" | PV15 voltage | 0.1 | 32044 | SHORT
"not use" | PV15 current | 0.01 | 32045 | SHORT
"not use" | PV16 voltage | 0.1 | 32046 | SHORT
"not use" | PV16 current | 0.01 | 32047 | SHORT
"not use" | PV17 voltage | 0.1 | 32048 | SHORT
"not use" | PV17 current | 0.01 | 32049 | SHORT
"not use" | PV18 voltage | 0.1 | 32050 | SHORT
"not use" | PV18 current | 0.01 | 32051 | SHORT
"not use" | PV19 voltage | 0.1 | 32052 | SHORT
"not use" | PV19 current | 0.01 | 32053 | SHORT
"not use" | PV20 voltage | 0.1 | 32054 | SHORT
"not use" | PV20 current | 0.01 | 32055 | SHORT
"not use" | Rated power | 0.001 | 30073 | SHORT
"not use" | Reactive power | 0.001 | 32082 | SW_INT
"not use" | Reactive power adjustment | 1 | 40196 | SHORT
"not use" | Reduced CO2 emission | 0.1 | 43524 | SHORT
"not use" | Shutdown time | 1 | 32093 | USHORT
"not use" | Startup time | 1 | 32091 | USHORT
"not use" | Total energy yield | 0.01 | 32106 | SW_UINT
"not use" | Line Voltage L1-L2 | 0.1 | 32066 | SHORT
"not use" | Line Voltage L2-L3 | 0.1 | 32067 | SHORT
"not use" | Line Voltage L3-L1 | 0.1 | 32068 | SHORT
"not use" | Efficiency | 0.0001 | 32086 | SHORT
"not use" | Alarm_1 | 1 | 32008 | SHORT
"not use" | Alarm_2 | 1 | 32009 | SHORT
"not use" | Alarm_3 | 1 | 32010 | SHORT
"use" | Power_adjustment | 0.1 | 35302 | SHORT