## Device list
| 1 | 2 | 3 | 4 | 5 |  | 6 | 7 | 8 | 9 | 10 | 11
[5 empty] | ABB | SMA | Huawei |  | Solar Edge
|  | Edge Computing | UPS Battery | Total | Inverter | Inverter | Smart Logger | Inverter | Inverter | Revenue Meter | Pyranometer | Grid Meter | PIC Middleware | Target Date install | Yoko Remark | Remark | mc id | API Key | Key ref
1 | Solar1 |  |  | 5 |  | 5 |  |  |  |  | 2 | 1 |  | Done | Solar1 ไม่มี internet |  |  | ygm_FUHz9QdfDPQpc1IaSsdn0OIERUmQ1kA2zM7k85yTeyM | O8sJQiAWhQTGDygbIDIea2u+QvxuaFJ+vHmdaAE+R2HcHnrfuD3bc82QeH/YFyaW32pTODZy/hLEWAKSwTijEg==
2 | VISTEC1 | 1 |  | 6 | 6 |  | - | - |  | 6 |  | 1 | ABB : SAX | 04/08/2026 13:30-15:30 | อยู่ Zone เดียวกัน | ใช้ Pyranometer Vistec2 | 0A775DA8A4CDE838 | ygm_Y9VkJob0alwMR5M52lszfyPE4iodYXAdy-JBYzwTGo0
3 | VISTEC2 |  |  | 11 | 10 |  | 1 | 1 |  | 3 | 1 |  | Huawei : NA
4 | KVIS | 1 |  | 1 | 1 |  |  |  |  | 1 |  | 1 | SMA : Nuttsu |  |  | ใช้ Pyranometer Vistec2
5 | Thaioil1 | 1 |  | 7 |  |  | 1 | 7 |  | 1 | 1 | 1 | SolarEdge : | 11/08/2026 13:30-16:30
6 | Thaioil2 | 1 |  | 5 |  |  | 1 | 5 |  | 4 | 1 | 2
7 | PTTOR MINBURI | 1 |  | 2 |  |  | 1 | 2 |  | 2 |  | 1
8 | PTTOR TALINCHAN | 1 |  | 1 |  |  | 1 | 1 |  | 1 |  | 1 |  | 04/08/2026 15:30-16:30 |  |  | 4A6E34BF9B08BB06 | ygm_2SahybmGZfoApzOLk65zwIxvyodAXD2f0yhIamiDTvU
9 | AICA | 1 | 1 | 30 |  |  | 2 | 30 |  | 2 | 1 | 1 |  |  |  |  | 30AD4DF0D366091B | ygm_00M8LbgAd96VvD56Nma1uccjIuvVkVbiqts87UbmWxI
10 | SURETEX | 1 | 1 | 17 |  |  | 1 | 17 |  | 2 | 1 | 1 |  | 05/08/2026 13:30-16:30 |  |  | 0A8E57B5C2B538A2 | ygm_RYsAtCAGydKABEGahLab43lBB9EHHeyyOouOL347RY4
11 | SUT | 1 | 1 | 31 |  |  | 3 | 31 |  | 6 | 2 | 1 |  |  |  |  | 4134D5B9244E5450 | ygm_MoAMjwOy_Xh1tuEbsZM4_82BG6LloSLMfaAvhFTNzrs
12 | PTIC | 1 | 1 | 2 |  |  | 1 | 2 |  | 1 | 1 | 1 |  |  |  | Add Smart Logger แยกของเราออกมา | FDA2301E661BB7CD | ygm_gY1iebmiCIELtHX1KsX4pS2LlsYDuBYy36VmiZ-BU10
13 | RASC | 1 | 1 | 3 |  |  | 1 | 3 |  | 1 | 1 | 1 |  |  | ตรวจสอบแล้วมี Internet |  | 9ED732AAAB654915 | ygm_09DCXdskJBE8_D8s0AhI7j7YdXiqG9Pzq23Pl7OpJeQ
14 | INI | 1 | 1 | 14 |  |  | 2 | 10 | 4 | 2 | 5 | 1 |  | 07/08/2026 13:30-16:30
15 | ENTER | 1 | 1 | 9 |  |  | 1 | 9 |  | 2 | 1 | 1
16 | FUTUREFLEX | 1 | 1 | 7 |  |  | 2 | 7 |  | 2 | 2 | 2
|  | 14 | 8
s

## IP List
|  | Building | No. | Equipment | Tag | Description | Capacity | Unit | Brand | Model | Serial | IP | Modbus Slave ID | Port
Vistec1 | VT1 | M1 | 1 | Inverter | VT1-M1-INV-01 | Buiding M1 Inverter | 127.05 | kWp | ABB | PVS-100-TL-POWER |  | 10.204.30.64 | 1 | 502
Vistec1 | VT1 | M2 | 1 | Inverter | VT1-M2-INV-01 | Buiding M2 Inverter | 127.05 | kWp | ABB | PVS-100-TL-POWER |  | 10.204.30.65 | 1 | 502
Vistec1 | VT1 | N | 1 | Inverter | VT1-N-INV-01 | Buiding N(Phase1) Inverter | 57.75 | kWp | ABB | PVS-50-TL-SX2 |  | 10.204.30.66 | 1 | 502
Vistec1 | VT1 | U | 1 | Inverter | VT1-U-INV-01 | Buiding U(Phase1) Inverter | 41.58 | kWp | ABB | PVS-50-TL-SX2 |  | 10.204.30.62 | 1 | 502
Vistec1 | VT1 | CP1 | 1 | Inverter | VT1-CP1-INV-01 | CP1 Buiding V Inverter | 103.95 | kWp | ABB | PVS-100-TL-POWER |  | 10.204.30.63 | 1 | 502
Vistec1 | VT1 | CP2 | 1 | Inverter | VT1-CP2-INV-01 | CP2 Buiding X Inverter | 48.51 | kWp | ABB | PVS-50-TL-SX2 |  | 10.204.30.61 | 1 | 502
Vistec1 | VT1 | M1 | 1 | Revenue Meter | VT1-M1-REV-01 | Building M1 Revenue Meter |  |  | EDMI | MK6E | 219150730 | 10.204.30.53 | 5 | 502
Vistec1 | VT1 | M2 | 1 | Revenue Meter | VT1-M2-REV-01 | Building M2 Revenue Meter |  |  | EDMI | MK6E | 219150723 | 10.204.30.54 | 3 | 502
Vistec1 | VT1 | V | 1 | Revenue Meter | VT1-V-REV-01 | Carpark Buiding V Revenue Meter |  |  | EDMI | MK6E | 219150729 | 10.204.30.52 | 4 | 502
Vistec1 | VT1 | X | 1 | Revenue Meter | VT1-X-REV-01 | Building U(Phase1) Revenue Meter |  |  | EDMI | MK6E | 219150735 | 10.204.30.50 | 8 | 502
Vistec1 | VT1 | N | 1 | Revenue Meter | VT1-N-REV-01 | Building N(Phase1) Revenue Meter |  |  | EDMI | MK6E | 219150736 | 10.204.30.55 | 10 | 502
Vistec1 | VT1 | U | 1 | Revenue Meter | VT1-U-REV-01 | Carpark Buiding X Revenue Meter |  |  | EDMI | MK6E | 219150734 | 10.204.30.51 | 9 | 502
Vistec1 | VT1 | V3 | 1 | Grid Meter | VT1-V3-GMT-01 | V3 Buiding Grid Meter | [5 empty] | 10.204.30.81 | 1 | 502
Vistec2 | VT2 | M3 | 1 | Inverter | VT2-M3-INV-01 | Building M3 Inverter No.1 | 110.88 | kWp | ABB | PVS-100-TL-POWER |  | 10.204.30.101 | 1 | 502
Vistec2 | VT2 | M3 | 2 | Inverter | VT2-M3-INV-02 | Building M3 Inverter No.2 | 52.8 | kWp | ABB | PVS-50-TL-SX2 |  | 10.204.30.102 | 1 | 502
Vistec2 | VT2 | M4 | 1 | Inverter | VT2-M4-INV-01 | Building M4 Inverter No.1 | 98.12 | kWp | ABB | PVS-100-TL-POWER |  | 10.204.30.103 | 1 | 502
Vistec2 | VT2 | M4 | 2 | Inverter | VT2-M4-INV-02 | Building M4 Inverter No.2 | 100.76 | kWp | ABB | PVS-100-TL-POWER |  | 10.204.30.104 | 1 | 502
Vistec2 | VT2 | N | 1 | Inverter | VT2-N-INV-01 | Building N(Phase2) Inverter | 66 | kWp | ABB | PVS-50-TL-SX2 |  | 10.204.30.67 | 1 | 502
Vistec2 | VT2 | U | 1 | Inverter | VT2-U-INV-01 | Building U(Phase2) Inverter | 95.04 | kWp | ABB | PVS-100-TL-POWER |  | 10.204.30.68 | 1 | 502
Vistec2 | VT2 | K | 1 | Inverter | VT2-K-INV-01 | Building K Inverter No.1 | 87.12 | kWp | ABB | PVS-100-TL-POWER |  | 10.204.30.105 | 1 | 502
Vistec2 | VT2 | K | 2 | Inverter | VT2-K-INV-02 | Building K Inverter No.2 | 87.12 | kWp | ABB | PVS-100-TL-POWER |  | 10.204.30.106 | 1 | 502
Vistec2 | VT2 | FT | 1 | Inverter | VT2-FT-INV-01 | Floating Inverter No.1 | 102.4 | kWp | ABB | PVS-100-TL-POWER |  | 10.204.30.107 | 1 | 502
Vistec2 | VT2 | CP-M3 | 1 | Inverter | VT2-CP-M3-INV-01 | Capark M3 Inverter | 23.76 | kWp | ABB | PVS-50-TL-SX2 |  | 10.204.30.108 | 1 | 502
Vistec2 | VT2 | CP-M3M4 | 1 | Inverter | VT2-CP-M3M4-INV-01 | Capark M3/M4 Inverter | 60.72 | kWp | Huawei | SUN2000-50KTL-M3 |  | 10.204.30.110 | 1 | 502
Vistec2 | VT2 | M4 | 1 | Pyranometer | VT2-M4-PRY-01 | Building M4 Pyranometer | [5 empty] | 10.204.30.110 | 6 | 502
Vistec2 | VT2 | M4 | 1 | Revenue Meter | VT2-M4-REV-01 | Building M4 Revenue Meter |  |  | EDMI | MK6E | 219014658 | 10.204.30.59 | 15 | 502
Vistec2 | VT2 | N | 1 | Revenue Meter | VT2-N-REV-01 | Buiding N(Phase2) Revenue Meter |  |  | EDMI | MK6E | 219014662 | 10.204.30.56 | 14 | 502
Vistec2 | VT2 | U | 1 | Revenue Meter | VT2-U-REV-01 | Buiding U(Phase2) Revenue Meter |  |  | EDMI | MK6E | 219014663 | 10.204.30.58 | 13 | 502
KVIS | KVIS | A | 1 | Inverter | KVIS-A-INV-01 | KVIS Inverter | 105.6 | kWp | ABB | PVS-100-TL-POWER |  | 10.205.30.100 | 1 | 502
KVIS | KVIS | A | 1 | Revenue Meter | KVIS-A-REV-01 | KVIS Revenue Meter |  |  | EDMI | MK6N | 219014664 | 10.205.30.90 | 19 | 502
KVIS | KVIS | V4 | 1 | Grid Meter | KVIS-V4-GMT-01 | KVIS Grid Meter | [5 empty] | 10.205.30.50 | 1 | 502
Thaioil1 | TO1 | EBC | 1 | Inverter | TO1-EBC-INV-01 | Inverter No.1 |  | kWp | Huawei | SUN2000-60KTL-M0 |  | 192.168.137.10 | 7 | 502
Thaioil1 | TO1 | EBC | 2 | Inverter | TO1-EBC-INV-02 | Inverter No.2 |  | kWp | Huawei | SUN2000-60KTL-M0 |  | 192.168.137.10 | 2 | 502
Thaioil1 | TO1 | EBC | 3 | Inverter | TO1-EBC-INV-03 | Inverter No.3 |  | kWp | Huawei | SUN2000-60KTL-M0 |  | 192.168.137.10 | 4 | 502
Thaioil1 | TO1 | EBC | 4 | Inverter | TO1-EBC-INV-04 | Inverter No.4 |  | kWp | Huawei | SUN2000-60KTL-M0 |  | 192.168.137.10 | 6 | 502
Thaioil1 | TO1 | EBC | 5 | Inverter | TO1-EBC-INV-05 | Inverter No.5 |  | kWp | Huawei | SUN2000-60KTL-M0 |  | 192.168.137.10 | 5 | 502
Thaioil1 | TO1 | EBC | 6 | Inverter | TO1-EBC-INV-06 | Inverter No.6 |  | kWp | Huawei | SUN2000-60KTL-M0 |  | 192.168.137.10 | 3 | 502
Thaioil1 | TO1 | EBC | 7 | Inverter | TO1-EBC-INV-07 | Inverter No.7 |  | kWp | Huawei | SUN2000-60KTL-M0 |  | 192.168.137.10 | 1 | 502
Thaioil1 | TO1 | EBC | 1 | Pyranometer | TO1-EBC-PRY-01 | Pyranometer | [5 empty] | 192.168.137.10 | 12 | 502
Thaioil2 | TO1 | EBC | 1 | Revenue Meter | TO1-EBC-REV-01 | Revenue Meter |  |  | EDMI | MK6E | 212296512 | 192.168.137.254 | 1 | 9000
Thaioil2 | TO1 | EBC | 1 | Grid Meter | TO1-EBC-GMT-01 | Grid Meter | [5 empty] | 192.168.137.10 | 8 | 502
Thaioil2 | TO2 |  | 1 | Inverter | TO2-INV-01 | Carpark DB1 Inverter No.1 | 107.46 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.127.10 | 6 | 502
Thaioil2 | TO2 |  | 2 | Inverter | TO2-INV-02 | Carpark DB4 Inverter No.2 | 99.9 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.127.10 | 5 | 502
Thaioil2 | TO2 |  | 3 | Inverter | TO2-INV-03 | Office DB2Inverter No.3 | 111.78 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.127.10 | 7 | 502
Thaioil2 | TO2 |  | 4 | Inverter | TO2-INV-04 | Office DB2 Inverter No.4 | 112.86 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.127.10 | 8 | 502
Thaioil2 | TO2 |  | 5 | Inverter | TO2-INV-05 | Auditrorium DB3 Inverter No.5 | 129.6 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.127.10 | 4 | 502
Thaioil2 | TO2 |  | 1 | Pyranometer | TO2-PRY-01 | Office Building Pyranometer | [5 empty] | 192.168.127.10 | 12 | 502
Thaioil2 | TO2 | DB1 | 1 | Revenue Meter | TO2-DB1-REV-01 | Carpark DB1 Revenue Meter |  |  | EDMI | MK6E | 251203492 | 192.168.127.42 | 1 | 502
Thaioil2 | TO2 | DB2 | 1 | Revenue Meter | TO2-DB2-REV-01 | Office DB2 Revenue Meter |  |  | EDMI | MK6E | 251203493 | 192.168.127.44 | 1 | 502
Thaioil2 | TO2 | DB3 | 1 | Revenue Meter | TO2-DB3-REV-01 | Auditrorium DB3 Revenue Meter |  |  | EDMI | MK6E | 251203494 | 192.168.127.46 | 1 | 502
Thaioil2 | TO2 | DB4 | 1 | Revenue Meter | TO2-DB4-REV-01 | Carpark DB4 Revenue Meter |  |  | EDMI | MK6E | 219150562 | 192.168.127.40 | 1 | 502
Thaioil2 | TO2 |  | 1 | Grid Meter | TO2-GMT-01 | Grid Meter Bus1 | [5 empty] | 192.168.127.10 | 3 | 502
Thaioil2 | TO2 |  | 2 | Grid Meter | TO2-GMT-02 | Grid Meter Bus2 | [5 empty] | 192.168.127.10 | 10 | 502
PTTOR MRB | PTTMB |  | 1 | Inverter | PTTMB-INV-01 | Fuel Station Inverter No.1 | 56 | kWp | Huawei | SUN2000-60KTL-M |  | 192.168.0.10 | 1 | 502
PTTOR MRB | PTTMB |  | 2 | Inverter | PTTMB-INV-02 | Market Zone Inverter No.2 | 72 | kWp | Huawei | SUN2000-60KTL-M |  | 192.168.0.10 | 5 | 502
PTTOR MRB | PTTMB |  | 1 | Revenue Meter | PTTMB-REV-01 | Fuel Station Revenue Meter No.1 |  |  | EDMI | MK6E | 251341652 | 192.168.0.4 | 1 | 9000
PTTOR MRB | PTTMB |  | 2 | Revenue Meter | PTTMB-REV-02 | Market Zone Revenue Meter No.2 |  |  | EDMI | MK6E | 251341653 | 192.168.0.4 | 2 | 502
PTTOR MRB | PTTMB |  | 1 | Grid Meter | PTTMB-GMT-01 | Grid Meter | [5 empty] | 192.168.0.10 | 4 | 502
PTTOR TLC | PTTTL |  | 1 | Inverter | PTTTL-INV-01 | Fuel Station Inverter No.1 | 48 | kWp | Huawei | SUN2000-60KTL-M |  | 192.168.0.10 | 1 | 502
PTTOR TLC | PTTTL |  | 1 | Revenue Meter | PTTTL-REV-01 | Fuel Station Revenue Meter No.1 |  |  | Mitsubishi | MX2-C41E | 9010563 | 192.168.0.20 | 163 | 502
PTTOR TLC | PTTTL |  | 1 | Grid Meter | PTTTL-GMT-01 | Grid Meter | [5 empty] | 192.168.0.10 | 2 | 502
AICA | AICA | DC | 1 | Inverter | AICA-DC-INV-01 | DC warehouse Inverter No.1 | 127.53 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 28 | 502
AICA | AICA | DC | 2 | Inverter | AICA-DC-INV-02 | DC warehouse Inverter No.2 | 127.53 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 27 | 502
AICA | AICA | DC | 3 | Inverter | AICA-DC-INV-03 | DC warehouse Inverter No.3 | 123.17 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 26 | 502
AICA | AICA | DC | 4 | Inverter | AICA-DC-INV-04 | DC warehouse Inverter No.4 | 127.53 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 25 | 502
AICA | AICA | DC | 5 | Inverter | AICA-DC-INV-05 | DC warehouse Inverter No.5 | 125.35 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 24 | 502
AICA | AICA | DC | 6 | Inverter | AICA-DC-INV-06 | DC warehouse Inverter No.6 | 120.99 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 23 | 502
AICA | AICA | DC | 7 | Inverter | AICA-DC-INV-07 | DC warehouse Inverter No.7 | 127.53 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 22 | 502
AICA | AICA | DC | 8 | Inverter | AICA-DC-INV-08 | DC warehouse Inverter No.8 | 123.17 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 21 | 502
AICA | AICA | DC | 9 | Inverter | AICA-DC-INV-09 | DC warehouse Inverter No.9 | 127.53 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 14 | 502
AICA | AICA | DC | 10 | Inverter | AICA-DC-INV-10 | DC warehouse Inverter No.10 | 132.98 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 19 | 502
AICA | AICA | DC | 11 | Inverter | AICA-DC-INV-11 | DC warehouse Inverter No.11 | 127.53 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 8 | 502
AICA | AICA | DC | 12 | Inverter | AICA-DC-INV-12 | DC warehouse Inverter No.12 | 125.35 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 17 | 502
AICA | AICA | DC | 13 | Inverter | AICA-DC-INV-13 | DC warehouse Inverter No.13 | 127.53 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 2 | 502
AICA | AICA | DC | 14 | Inverter | AICA-DC-INV-14 | DC warehouse Inverter No.14 | 132.98 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 15 | 502
AICA | AICA | DC | 15 | Inverter | AICA-DC-INV-15 | DC warehouse Inverter No.15 | 132.435 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 13 | 502
AICA | AICA | DC | 16 | Inverter | AICA-DC-INV-16 | DC warehouse Inverter No.16 | 127.53 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 13 | 502
AICA | AICA | DC | 17 | Inverter | AICA-DC-INV-17 | DC warehouse Inverter No.17 | 127.53 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 4 | 502
AICA | AICA | DC | 18 | Inverter | AICA-DC-INV-18 | DC warehouse Inverter No.18 | 133.525 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 11 | 502
AICA | AICA | DC | 19 | Inverter | AICA-DC-INV-19 | DC warehouse Inverter No.19 | 132.98 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 3 | 502
AICA | AICA | DC | 20 | Inverter | AICA-DC-INV-20 | DC warehouse Inverter No.20 | 137.34 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 9 | 502
AICA | AICA | DC | 21 | Inverter | AICA-DC-INV-21 | DC warehouse Inverter No.21 | 127.53 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 11 | 502
AICA | AICA | DC | 22 | Inverter | AICA-DC-INV-22 | DC warehouse Inverter No.22 | 134.07 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 10 | 502
AICA | AICA | DC | 23 | Inverter | AICA-DC-INV-23 | DC warehouse Inverter No.23 | 137.34 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 5 | 502
AICA | AICA | DC | 24 | Inverter | AICA-DC-INV-24 | DC warehouse Inverter No.24 | 133.525 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 1 | 502
AICA | AICA | DC | 25 | Inverter | AICA-DC-INV-25 | DC warehouse Inverter No.25 | 137.34 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 6 | 502
AICA | AICA | DC | 26 | Inverter | AICA-DC-INV-26 | DC warehouse Inverter No.26 | 134.07 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 7 | 502
AICA | AICA | DC | 27 | Inverter | AICA-DC-INV-27 | DC warehouse Inverter No.27 | 137.34 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 9 | 502
AICA | AICA | DC | 28 | Inverter | AICA-DC-INV-28 | DC warehouse Inverter No.28 | 132.98 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 12 | 502
AICA | AICA | DRY | 1 | Inverter | AICA-DRY-INV-01 | DRYMIX Inverter No.1 | 120.45 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 15 | 502
AICA | AICA | DRY | 2 | Inverter | AICA-DRY-INV-02 | DRYMIX Inverter No.2 | 120.45 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.20 | 16 | 502
AICA | AICA | DC | 1 | Revenue Meter | AICA-DC-REV-01 | DC warehouse Revenue Meter |  |  | EDMI | MK6E | 250710616 | 192.168.186 | 1 | 502
AICA | AICA | DRY | 2 | Revenue Meter | AICA-DRY-REV-02 | DRYMIX Revenue Meter |  |  | EDMI | MK6E | 920809102 | 192.168.1.85 | 1 | 502
AICA | AICA | DC | 1 | Pyranometer | AICA-DC-PRY-01 | DRYMIX Pyranometer | [5 empty] | 192.168.1.10 | 42 | 502
AICA | AICA |  | 1 | Grid Meter | AICA-GMT-01 | Sub115 Grid Meter | [5 empty] | 192.168.1.10 | 41 | 502
SURETEX | SRT | S1 | 1 | Inverter | SRT-S1-INV-01 | Inverter Station Inverter No.1 | 192.8 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 46 | 502
SURETEX | SRT | S1 | 2 | Inverter | SRT-S1-INV-02 | Inverter Station Inverter No.2 | 186.8 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 12 | 502
SURETEX | SRT | S1 | 3 | Inverter | SRT-S1-INV-03 | Inverter Station Inverter No.3 | 190.6 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 7 | 502
SURETEX | SRT | S1 | 4 | Inverter | SRT-S1-INV-04 | Inverter Station Inverter No.4 | 194.4 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 11 | 502
SURETEX | SRT | S1 | 5 | Inverter | SRT-S1-INV-05 | Inverter Station Inverter No.5 | 189.5 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 10 | 502
SURETEX | SRT | S1 | 6 | Inverter | SRT-S1-INV-06 | Inverter Station Inverter No.6 | 194.4 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 8 | 502
SURETEX | SRT | S1 | 7 | Inverter | SRT-S1-INV-07 | Inverter Station Inverter No.7 | 179.3 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 5 | 502
SURETEX | SRT | S1 | 8 | Inverter | SRT-S1-INV-08 | Inverter Station Inverter No.8 | 191.2 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 14 | 502
SURETEX | SRT | S1 | 9 | Inverter | SRT-S1-INV-09 | Inverter Station Inverter No.9 | 191.2 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 13 | 502
SURETEX | SRT | S1 | 10 | Inverter | SRT-S1-INV-10 | Inverter Station Inverter No.10 | 194.4 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 4 | 502
SURETEX | SRT | S1 | 11 | Inverter | SRT-S1-INV-11 | Inverter Station Inverter No.11 | 194.4 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 9 | 502
SURETEX | SRT | S1 | 12 | Inverter | SRT-S1-INV-12 | Inverter Station Inverter No.12 | 191.2 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 6 | 502
SURETEX | SRT | S1 | 13 | Inverter | SRT-S1-INV-13 | Inverter Station Inverter No.13 | 192.2 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 3 | 502
SURETEX | SRT | S1 | 14 | Inverter | SRT-S1-INV-14 | Inverter Station Inverter No.14 | 189 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 37 | 502
SURETEX | SRT | S1 | 15 | Inverter | SRT-S1-INV-15 | Inverter Station Inverter No.15 | 192.8 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.3 | 36 | 502
SURETEX | SRT | S2 | 16 | Inverter | SRT-S2-INV-16 | Substation4 Inverter No.16 | 78.3 | kWp | Huawei | SUN2000-60KTL-M0 |  | 192.168.1.3 | 31 | 502
SURETEX | SRT | S2 | 17 | Inverter | SRT-S2-INV-17 | Substation4 Inverter No.17 | 72.9 | kWp | Huawei | SUN2000-60KTL-M0 |  | 192.168.1.3 | 32 | 502
SURETEX | SRT | S1 | 1 | Revenue Meter | SRT-S1-REV-01 | Inverter Station Revenue Meter |  |  | EDMI | MK6E | 251203497 | 192.168.1.51 | 1 | 502
SURETEX | SRT | S2 | 1 | Revenue Meter | SRT-S2-REV-01 | Substation4 Revenue Meter |  |  | EDMI | MK6E | 251203585 | 192.168.1.52 | 1 | 502
SURETEX | SRT |  | 1 | Pyranometer | SRT-PRY-01 | Suretex Pyranometer | [5 empty] | 192.168.1.3 | 45 | 502
SURETEX | SRT |  | 1 | Grid Meter | SRT-GMT-01 | 33kV Grid Meter | [5 empty] | 192.168.1.3 | 35 | 502
Suranaree | SUT | CL1 | 1 | Revenue Meter | SUT-CL1-REV-01 | Class Room1 Revenue Meter |  |  | EDMI | MK6E | 251203642 | 10.12.7.174 | 1 | 502
Suranaree | SUT | SV | 1 | Revenue Meter | SUT-SV-REV-01 | Suranivet5 Revenue Meter |  |  | EDMI | MK6E | 251203644 | 10.12.7.176 | 1 | 502
Suranaree | SUT | SC | 1 | Revenue Meter | SUT-SC-REV-01 | Suraueng Chai Revenue Meter |  |  | EDMI | MK6E | 251203641 | 10.12.7.175 | 1 | 502
Suranaree | SUT | FT | 1 | Revenue Meter | SUT-FT-REV-01 | Floating Revenue Meter |  |  | EDMI | MK6E | 251203501 | 10.12.7.171 | 1 | 502
Suranaree | SUT | F10 | 1 | Revenue Meter | SUT-F10-REV-01 | F10 Revenue Meter |  |  | EDMI | MK6E | 251203640 | 10.12.7.172 | 1 | 502
Suranaree | SUT | F12 | 1 | Revenue Meter | SUT-F12-REV-01 | F12 Revenue Meter |  |  | EDMI | MK6E | 251203643 | 10.12.7.173 | 1 | 502
Suranaree | SUT | CL1 | 1 | Inverter | SUT-CL1-INV-01 | Class Room1 Inverter No.1 | 138.24 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.141 | 9 | 502
Suranaree | SUT | CL1 | 2 | Inverter | SUT-CL1-INV-02 | Class Room1 Inverter No.2 | 138.24 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.141 | 8 | 502
Suranaree | SUT | CL1 | 3 | Inverter | SUT-CL1-INV-03 | Class Room1 Inverter No.3 | 138.24 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.141 | 10 | 502
Suranaree | SUT | CL1 | 4 | Inverter | SUT-CL1-INV-04 | Class Room1 Inverter No.4 | 110.7 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.141 | 11 | 502
Suranaree | SUT | SC | 1 | Inverter | SUT-SC-INV-01 | Surareang Chai Inverter No.1 | 112.32 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.142 | 4 | 502
Suranaree | SUT | SC | 2 | Inverter | SUT-SC-INV-02 | Surareang Chai Inverter No.2 | 112.32 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.142 | 7 | 502
Suranaree | SUT | SC | 3 | Inverter | SUT-SC-INV-03 | Surareang Chai Inverter No.3 | 120.96 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.142 | 6 | 502
Suranaree | SUT | SC | 4 | Inverter | SUT-SC-INV-04 | Surareang Chai Inverter No.4 | 120.96 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.142 | 5 | 502
Suranaree | SUT | CP | 1 | Inverter | SUT-CP-INV-01 | Capark Inverter No.1 | 32.4 | kWp | Huawei | SUN2000-30KTL-M3 |  | 10.12.7.141 | 7 | 502
Suranaree | SUT | CP | 2 | Inverter | SUT-CP-INV-02 | Capark Inverter No.2 | 320.4 | kWp | Huawei | SUN2000-30KTL-M3 |  | 10.12.7.141 | 6 | 502
Suranaree | SUT | FT | 1 | Inverter | SUT-FT-INV-01 | Floating Inverter No.1 | 252.72 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 7 | 502
Suranaree | SUT | FT | 2 | Inverter | SUT-FT-INV-02 | Floating Inverter No.2 | 252.72 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 15 | 502
Suranaree | SUT | FT | 3 | Inverter | SUT-FT-INV-03 | Floating Inverter No.3 | 252.72 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 4 | 502
Suranaree | SUT | FT | 4 | Inverter | SUT-FT-INV-04 | Floating Inverter No.4 | 252.72 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 5 | 502
Suranaree | SUT | FT | 5 | Inverter | SUT-FT-INV-05 | Floating Inverter No.5 | 272.16 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 9 | 502
Suranaree | SUT | FT | 6 | Inverter | SUT-FT-INV-06 | Floating Inverter No.6 | 272.16 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 2 | 502
Suranaree | SUT | FT | 7 | Inverter | SUT-FT-INV-07 | Floating Inverter No.7 | 272.16 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 11 | 502
Suranaree | SUT | FT | 8 | Inverter | SUT-FT-INV-08 | Floating Inverter No.8 | 272.16 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 10 | 502
Suranaree | SUT | FT | 9 | Inverter | SUT-FT-INV-09 | Floating Inverter No.9 | 272.16 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 13 | 502
Suranaree | SUT | FT | 10 | Inverter | SUT-FT-INV-10 | Floating Inverter No.10 | 263.52 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 6 | 502
Suranaree | SUT | FT | 11 | Inverter | SUT-FT-INV-11 | Floating Inverter No.11 | 272.16 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 3 | 502
Suranaree | SUT | FT | 12 | Inverter | SUT-FT-INV-12 | Floating Inverter No.12 | 272.16 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 14 | 502
Suranaree | SUT | FT | 13 | Inverter | SUT-FT-INV-13 | Floating Inverter No.13 | 272.16 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 17 | 502
Suranaree | SUT | FT | 14 | Inverter | SUT-FT-INV-14 | Floating Inverter No.14 | 272.16 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 8 | 502
Suranaree | SUT | FT | 15 | Inverter | SUT-FT-INV-15 | Floating Inverter No.15 | 272.16 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 12 | 502
Suranaree | SUT | FT | 16 | Inverter | SUT-FT-INV-16 | Floating Inverter No.16 | 272.16 | kWp | Huawei | SUN2000-215KTL-H0 |  | 10.12.7.140 | 16 | 502
Suranaree | SUT | F12 | 1 | Inverter | SUT-F12-INV-01 | F12 Inverter No.1 | 138.24 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.141 | 1 | 502
Suranaree | SUT | F12 | 2 | Inverter | SUT-F12-INV-02 | F12 Inverter No.2 | 138.24 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.141 | 2 | 502
Suranaree | SUT | F12 | 3 | Inverter | SUT-F12-INV-03 | F12 Inverter No.3 | 138.24 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.141 | 3 | 502
Suranaree | SUT | F10 | 1 | Inverter | SUT-F10-INV-01 | F10 Inverter No.3 | 116.64 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.141 | 4 | 502
Suranaree | SUT | SV5 | 1 | Inverter | SUT-SV5-INV-01 | Suranivet5 Inverter | 138.24 | kWp | Huawei | SUN2000-100KTL-M1 |  | 10.12.7.142 | 8 | 502
Suranaree | SUT | CL1 | 1 | Pyranometer | SUT-CL1-PRY-01 | Class Room1 Pyranometer | [5 empty] | 10.12.7.141 | 24 | 502
Suranaree | SUT | FT | 1 | Pyranometer | SUT-FT-PRY-01 | Floating Pyranometer | [5 empty] | 10.12.7.140 | 18 | 502
Suranaree | SUT | 115KV | 1 | Grid Meter | SUT-115KV-GMT-01 | 115kV Grid Meter | [5 empty] | 10.12.7.142 | 1 | 502
PTTEP PTIC | PTIC |  | 1 | Inverter | PTIC-INV-01 | Inverter No.1 | 124.26 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 12 | 502
PTTEP PTIC | PTIC |  | 2 | Inverter | PTIC-INV-02 | Inverter No.2 | 113.36 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 11 | 502
PTTEP PTIC | PTIC |  | 1 | Pyranometer | PTIC-PRY-01 | Pyranometer | [5 empty] | 192.168.1.10 | 14 | 502
PTTEP PTIC | PTIC |  | 1 | Revenue Meter | PTIC-REV-01 | Revenue Meter |  |  | EDMI | MK6E | 251508494 | 192.168.1.12 | 1 | 502
PTTEP PTIC | PTIC |  | 1 | Grid Meter | PTIC-GMT-01 | 22kV Grid Meter | [5 empty] | 192.168.1.10 | 10 | 502
PTTEP RASC | RASC |  | 1 | Inverter | RASC-INV-01 | Inverter No.1 | 116.64 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 3 | 502
PTTEP RASC | RASC |  | 2 | Inverter | RASC-INV-02 | Inverter No.2 | 116.64 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.10 | 14 | 502
PTTEP RASC | RASC |  | 3 | Inverter | RASC-INV-03 | Inverter No.3 | 48.6 | kWp | Huawei | SUN2000-40KTL-M3 |  | 192.168.1.10 | 2 | 502
PTTEP RASC | RASC |  | 1 | Pyranometer | RASC-PRY-01 | Pyranometer | [5 empty] | 192.168.1.10 | 13 | 502
PTTEP RASC | RASC |  | 1 | Revenue Meter | RASC-REV-01 | Revenue Meter |  |  | EDMI | MK6E | 251508563 | 192.168.1.30 | 1 | 502
PTTEP RASC | RASC |  | 1 | Grid Meter | RASC-GMT-01 | Grid Meter | [5 empty] | 192.168.1.10 | 12 | 502
ENTER | ENT | MS1 | 1 | Inverter | ENT-MS1-INV-01 | Inverter No.1 | 55 | kWp | Huawei | SUN2000-50KTL-M3 |  | 192.168.1.10 | 5 | 502
ENTER | ENT | MS1 | 2 | Inverter | ENT-MS1-INV-02 | Inverter No.2 | 53.9 | kWp | Huawei | SUN2000-50KTL-M3 |  | 192.168.1.10 | 6 | 502
ENTER | ENT | MS2 | 3 | Inverter | ENT-MS2-INV-03 | Inverter No.3 | 66 | kWp | Huawei | SUN2000-50KTL-M3 |  | 192.168.1.10 | 7 | 502
ENTER | ENT | CP1 | 4 | Inverter | ENT-CP1-INV-04 | Inverter No.4 | 67.1 | kWp | Huawei | SUN2000-50KTL-M3 |  | 192.168.1.10 | 8 | 502
ENTER | ENT | CP2 | 5 | Inverter | ENT-CP2-INV-05 | Inverter No.5 | 59.4 | kWp | Huawei | SUN2000-50KTL-M3 |  | 192.168.1.10 | 9 | 502
ENTER | ENT | CP2 | 6 | Inverter | ENT-CP2-INV-06 | Inverter No.6 | 59.4 | kWp | Huawei | SUN2000-50KTL-M3 |  | 192.168.1.10 | 10 | 502
ENTER | ENT | CP2 | 7 | Inverter | ENT-CP2-INV-07 | Inverter No.7 | 59.4 | kWp | Huawei | SUN2000-50KTL-M3 |  | 192.168.1.10 | 11 | 502
ENTER | ENT | CP2 | 8 | Inverter | ENT-CP2-INV-08 | Inverter No.8 | 59.4 | kWp | Huawei | SUN2000-50KTL-M3 |  | 192.168.1.10 | 1 | 502
ENTER | ENT | EV | 9 | Inverter | ENT-EV-INV-09 | Inverter No.9 | 68.2 | kWp | Huawei | SUN2000-50KTL-M3 |  | 192.168.1.10 | 4 | 502
ENTER | ENT | MS1 | 1 | Revenue Meter | ENT-MS1-REV-01 | Inverter Station Revenue Meter |  |  | EDMI | MK6E | 251508511 | 192.168.1.60 | 1 | 502
ENTER | ENT | MS2 | 1 | Revenue Meter | ENT-MS2-REV-01 | Carpark Revenue Meter |  |  | EDMI | MK6E | 251508510 | 192.168.1.61 | 2 | 502
ENTER | ENT |  | 1 | Pyranometer | ENT-PRY-01 | Pyranometer | [5 empty] | 192.168.1.10 | 3 | 502
ENTER | ENT |  | 1 | Grid Meter | ENT-GMT-01 | Grid Meter | [5 empty] | 192.168.1.10 | 2 | 502
PTT INI | INI | BP | 1 | Inverter | INI-BP-INV-01 | Big Pond Inverter No.1 | 238.68 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.10 | 4 | 502
PTT INI | INI | BP | 2 | Inverter | INI-BP-INV-02 | Big Pond Inverter No.2 | 238.68 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.10 | 3 | 502
PTT INI | INI | BP | 3 | Inverter | INI-BP-INV-03 | Big Pond Inverter No.3 | 238.68 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.10 | 14 | 502
PTT INI | INI | BP | 4 | Inverter | INI-BP-INV-04 | Big Pond Inverter No.4 | 229.5 | kWp | Huawei | SUN2000-185KTL-H1 |  | 192.168.1.10 | 5 | 502
PTT INI | INI | SP | 1 | Inverter | INI-SP-INV-01 | Small Pond Inverter No.1 | 88.7 | kWp | Solaredge | SE82.8K-RW0P0BNU4 |  | 192.168.1.46 | 1 | 502
PTT INI | INI | SP | 2 | Inverter | INI-SP-INV-02 | Small Pond Inverter No.2 | 88.7 | kWp | Solaredge | SE82.8K-RW0P0BNU4 |  | 192.168.1.46 | 2 | 502
PTT INI | INI | SP | 3 | Inverter | INI-SP-INV-03 | Small Pond Inverter No.3 | 88.7 | kWp | Solaredge | SE82.8K-RW0P0BNU4 |  | 192.168.1.46 | 3 | 502
PTT INI | INI | SP | 4 | Inverter | INI-SP-INV-04 | Small Pond Inverter No.4 | 88.7 | kWp | Solaredge | SE82.8K-RW0P0BNU4 |  | 192.168.1.46 | 4 | 502
PTT INI | INI | BP | 1 | Pyranometer | INI-BP-PRY-01 | Big Pond Pyranometer | [5 empty] | 192.168.1.10 | 12 | 502
PTT INI | INI | LC | 1 | Inverter | INI-LC-INV-01 | Learning Center Pump House | 25.2 | kWp | Huawei | SUN2000-20KTL-M2 |  | 192.168.1.10 | 10 | 502
PTT INI | INI | LC | 2 | Inverter | INI-LC-INV-02 | Learning Center Big Pond | 25.2 | kWp | Huawei | SUN2000-20KTL-M2 |  | 192.168.1.10 | 9 | 502
PTT INI | INI | LC | 3 | Inverter | INI-LC-INV-03 | Learning Center Ground Mount | 25.2 | kWp | Huawei | SUN2000-20KTL-M2 |  | 192.168.1.10 | 8 | 502
PTT INI | INI | LC | 4 | Inverter | INI-LC-INV-04 | Learning Center Tracking | 25.2 | kWp | Huawei | SUN2000-20KTL-M2 |  | 192.168.1.10 | 11 | 502
PTT INI | INI | LC | 1 | Pyranometer | INI-LC-PRY-01 | Learning Center Pyranometer Ground Mount | [5 empty] | 192.168.1.10 | 12 | 502
PTT INI | INI | LC | 2 | Pyranometer | INI-LC-PRY-02 | Learning Center Pyranometer Tracking | [5 empty] | 192.168.1.10 | 13 | 502
PTT INI | INI | UN | 1 | Revenue Meter | INI-UN-REV-01 | Unit Substation Revenue Meter |  |  | EDMI | MK6E | 251203623 | 192.168.1.40 | 2 | 502
PTT INI | INI | UB | 1 | Inverter | INI-UB-INV-01 | UB Inverter No.1 | 140.4 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.11 | 5 | 502
PTT INI | INI | UB | 2 | Inverter | INI-UB-INV-02 | UB Inverter No.2 | 140.4 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.1.11 | 6 | 502
PTT INI | INI | UB | 1 | Pyranometer | INI-UB-PRY-01 | POA UB Building Pyranometer | [5 empty] | 192.168.1.11 | 12 | 502
PTT INI | INI | UB | 2 | Pyranometer | INI-UB-PRY-02 | GHI UB Building Pyranometer | [5 empty] | 192.168.1.11 | 12 | 502
PTT INI | INI | UB | 1 | Revenue Meter | INI-UB-REV-01 | UB Building Revenue Meter |  |  | EDMI | MK6E | 251203612 | 192.168.1.41 | 1 | 502
PTT INI | INI | 115kV | 1 | Grid Meter | INI-115kV-GMT-01 | Sub 115kV Grid Meter | [5 empty] | 192.168.1.47 | 33 | 502
FUTURE FLEX | FTF |  | 1 | Inverter | FTF-INV-01 | 1st Floor Inverter No.1 | 127.74 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.0.9 | 5 | 502
FUTURE FLEX | FTF |  | 2 | Inverter | FTF-INV-02 | 1st Floor Inverter No.2 | 129.6 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.0.9 | 4 | 502
FUTURE FLEX | FTF |  | 3 | Inverter | FTF-INV-03 | 1st Floor Inverter No.3 | 129.6 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.0.9 | 3 | 502
FUTURE FLEX | FTF |  | 4 | Inverter | FTF-INV-04 | 1st Floor Inverter No.4 | 131.7 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.0.9 | 1 | 502
FUTURE FLEX | FTF |  | 5 | Inverter | FTF-INV-05 | 1st Floor Inverter No.5 | 129.6 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.0.9 | 2 | 502
FUTURE FLEX | FTF |  | 1 | Pyranometer | FTF-PRY-01 | 1st Pyranometer | [5 empty] | 192.168.0.9 |  | 502
FUTURE FLEX | FTF |  | 1 | Revenue Meter | FTF-REV-01 | 1st Revenue Meter |  |  | EDMI | MK6E | 251203553 | 192.168.0.31 | 1 | 502
FUTURE FLEX | FTF |  | 1 | Grid Meter | FTF-GMT-01 | 1st Grid Meter | [5 empty] | 192.168.0.9 | 13 | 502
FUTURE FLEX | FTF |  | 6 | Inverter | FTF-INV-06 | 2nd Floor Inverter No.6 | 129.6 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.0.10 | 2 | 502
FUTURE FLEX | FTF |  | 7 | Inverter | FTF-INV-07 | 2nd Floor Inverter No.7 | 129.6 | kWp | Huawei | SUN2000-100KTL-M1 |  | 192.168.0.10 | 1 | 502
FUTURE FLEX | FTF |  | 2 | Pyranometer | FTF-PRY-02 | 2nd Pyranometer | [5 empty] | 192.168.0.10 |  | 502
FUTURE FLEX | FTF |  | 2 | Revenue Meter | FTF-REV-02 | 2nd Revenue Meter |  |  | EDMI | MK6E | 251203554 | 192.168.0.30 | 2 | 502
FUTURE FLEX | FTF |  | 2 | Grid Meter | FTF-GMT-02 | 2nd Grid Meter | [5 empty] | 192.168.0.10 | 30 | 502

## PVS100
State | Description | Factor | Register | Data Type | Remark
"not use" | Amps | 1 | 40072 | USHORT
"not use" | Amps PhaseA | 0.1 | 40073 | USHORT
"not use" | Amps PhaseB | 0.1 | 40074 | USHORT
"not use" | Amps PhaseC | 0.1 | 40075 | USHORT
"not use" | A_SF | 1 | 40076 | USHORT
"not use" | Phase Voltage AB | 0.1 | 40077 | USHORT
"not use" | Phase Voltage BC | 0.1 | 40078 | USHORT
"not use" | Phase Voltage CA | 0.1 | 40079 | USHORT
"not use" | Phase Voltage AN | 0.1 | 40080 | USHORT
"not use" | Phase Voltage BN | 0.1 | 40081 | USHORT
"not use" | Phase Voltage CN | 0.1 | 40082 | USHORT
"not use" | V_SF | 1 | 40083 | USHORT
"use" | Watts | 0.01 | 40084 | SHORT
"not use" | W_SF | 1 | 40085 | SHORT
"not use" | Hz | 0.01 | 40086 | USHORT
"not use" | Hz_SF | 1 | 40087 | USHORT
"not use" | VA | 0.01 | 40088 | SHORT
"not use" | VA_SF | 1 | 40089 | SHORT
"not use" | Var | 0.01 | 40090 | SHORT
"not use" | VAr_SF | 1 | 40091 | SHORT
"not use" | PF | 0.0001 | 40092 | SHORT
"not use" | PF_SF | 1 | 40093 | SHORT
"not use" | WattHours | 0.01 | 40094 | SW_INT
"not use" | WH_SF | 1 | 40096 | USHORT
"not use" | DC Amps | 0.1 | 40097 | USHORT
"not use" | DCA_SF | 1 | 40098 | USHORT
"not use" | DC Voltage | 0.1 | 40099 | USHORT
"not use" | DCV_SF | 1 | 40100 | USHORT
"not use" | DC Watts | 0.01 | 40101 | SHORT
"not use" | DCW_SF | 1 | 40102 | SHORT
"not use" | Cabinet Temperature | 0.1 | 40103 | SHORT
"not use" | Heat Sink Temperature | 0.1 | 40104 | SHORT
"not use" | Transformer Temperature | 0.1 | 40105 | SHORT
"not use" | Other Temperature | 0.1 | 40106 | SHORT
"not use" | Tmp_SF | 1 | 40107 | SHORT
"use" | Operating State | 1 | 40108 | USHORT | 1: Off 2: Sleeping 3: Starting 4: Normal 5: Throttled(Derating) 6: Shutdown 7: Fault 8: Standby
"not use" | ActWh | 1 | 40187 | FLOAT
"not use" | DC Current_1 | 0.1 | 41123 | USHORT
"not use" | DC Voltage_1 | 0.1 | 41124 | USHORT
"not use" | DC Power_1 | 0.01 | 41125 | USHORT
"not use" | DC Current_2 | 0.1 | 41143 | USHORT
"not use" | DC Voltage_2 | 0.1 | 41144 | USHORT
"not use" | DC Power_2 | 0.01 | 41145 | USHORT
"not use" | DC Current_3 | 0.1 | 41163 | USHORT
"not use" | DC Voltage_3 | 0.1 | 41164 | USHORT
"not use" | DC Power_3 | 0.01 | 41165 | USHORT
"not use" | DC Current_4 | 0.1 | 41183 | USHORT
"not use" | DC Voltage_4 | 0.1 | 41184 | USHORT
"not use" | DC Power_4 | 0.01 | 41185 | USHORT
"not use" | DC Current_5 | 0.1 | 41203 | USHORT
"not use" | DC Voltage_5 | 0.1 | 41204 | USHORT
"not use" | DC Power_5 | 0.01 | 41205 | USHORT
"not use" | DC Current_6 | 0.1 | 41223 | USHORT
"not use" | DC Voltage_6 | 0.1 | 41224 | USHORT
"not use" | DC Power_6 | 0.01 | 41225 | USHORT
"not use" | String Input Current_1 | 0.1 | 41257 | SHORT
"not use" | String Input Current_2 | 0.1 | 41265 | SHORT
"not use" | String Input Current_3 | 0.1 | 41273 | SHORT
"not use" | String Input Current_4 | 0.1 | 41281 | SHORT
"not use" | String Input Current_5 | 0.1 | 41289 | SHORT
"not use" | String Input Current_6 | 0.1 | 41297 | SHORT
"not use" | String Input Current_7 | 0.1 | 41305 | SHORT
"not use" | String Input Current_8 | 0.1 | 41313 | SHORT
"not use" | String Input Current_9 | 0.1 | 41321 | SHORT
"not use" | String Input Current_10 | 0.1 | 41329 | SHORT
"not use" | String Input Current_11 | 0.1 | 41337 | SHORT
"not use" | String Input Current_12 | 0.1 | 41345 | SHORT
"not use" | String Input Current_13 | 0.1 | 41353 | SHORT
"not use" | String Input Current_14 | 0.1 | 41361 | SHORT
"not use" | String Input Current_15 | 0.1 | 41369 | SHORT
"not use" | String Input Current_16 | 0.1 | 41377 | SHORT
"not use" | String Input Current_17 | 0.1 | 41385 | SHORT
"not use" | String Input Current_18 | 0.1 | 41393 | SHORT
"not use" | String Input Current_19 | 0.1 | 41401 | SHORT
"not use" | String Input Current_20 | 0.1 | 41409 | SHORT
"not use" | String Input Current_21 | 0.1 | 41417 | SHORT
"not use" | String Input Current_22 | 0.1 | 41425 | SHORT
"not use" | String Input Current_23 | 0.1 | 41433 | SHORT
"not use" | String Input Current_24 | 0.1 | 41441 | SHORT
"not use" | EVENT_1 | 1 | 40110 | LONG
"use" | %Command Watt Limit | 0.1 | 40233 | USHORT

## PVS50
State | Description | Factor | Register | Data Type | Remark
"not use" | Amps | 1 | 40072 | USHORT
"not use" | Amps PhaseA | 0.1 | 40073 | USHORT
"not use" | Amps PhaseB | 0.1 | 40074 | USHORT
"not use" | Amps PhaseC | 0.1 | 40075 | USHORT
"not use" | A_SF | 1 | 40076 | USHORT
"not use" | Phase Voltage AB | 0.1 | 40077 | USHORT
"not use" | Phase Voltage BC | 0.1 | 40078 | USHORT
"not use" | Phase Voltage CA | 0.1 | 40079 | USHORT
"not use" | Phase Voltage AN | 0.1 | 40080 | USHORT
"not use" | Phase Voltage BN | 0.1 | 40081 | USHORT
"not use" | Phase Voltage CN | 0.1 | 40082 | USHORT
"not use" | V_SF | 1 | 40083 | USHORT
"use" | Watts | 0.01 | 40084 | SHORT
"not use" | W_SF | 1 | 40085 | SHORT
"not use" | Hz | 0.01 | 40086 | USHORT
"not use" | Hz_SF | 1 | 40087 | USHORT
"not use" | VA | 0.01 | 40088 | SHORT
"not use" | VA_SF | 1 | 40089 | SHORT
"not use" | Var | 0.01 | 40090 | SHORT
"not use" | VAr_SF | 1 | 40091 | SHORT
"not use" | PF | 0.0001 | 40092 | SHORT
"not use" | PF_SF | 1 | 40093 | SHORT
"not use" | WattHours | 0.01 | 40094 | SW_INT
"not use" | WH_SF | 1 | 40096 | USHORT
"not use" | DC Amps | 0.1 | 40097 | USHORT
"not use" | DCA_SF | 1 | 40098 | USHORT
"not use" | DC Voltage | 0.1 | 40099 | USHORT
"not use" | DCV_SF | 1 | 40100 | USHORT
"not use" | DC Watts | 0.01 | 40101 | SHORT
"not use" | DCW_SF | 1 | 40102 | SHORT
"not use" | Cabinet Temperature | 0.1 | 40103 | SHORT
"not use" | Heat Sink Temperature | 0.1 | 40104 | SHORT
"not use" | Transformer Temperature | 0.1 | 40105 | SHORT
"not use" | Other Temperature | 0.1 | 40106 | SHORT
"not use" | Tmp_SF | 1 | 40107 | SHORT
"use" | Operating State | 1 | 40108 | USHORT | 1: Off 2: Sleeping 3: Starting 4: Normal 5: Throttled(Derating) 6: Shutdown 7: Fault 8: Standby
"not use" | ActWh | 1 | 40187 | FLOAT
"not use" | DC Current_1 | 0.1 | 41123 | USHORT
"not use" | DC Voltage_1 | 0.1 | 41124 | USHORT
"not use" | DC Power_1 | 0.01 | 41125 | USHORT
"not use" | DC Current_2 | 0.1 | 41143 | USHORT
"not use" | DC Voltage_2 | 0.1 | 41144 | USHORT
"not use" | DC Power_2 | 0.01 | 41145 | USHORT
"not use" | DC Current_3 | 0.1 | 41163 | USHORT
"not use" | DC Voltage_3 | 0.1 | 41164 | USHORT
"not use" | DC Power_3 | 0.01 | 41165 | USHORT
"not use" | EVENT_1 | 1 | 40110 | LONG
"use" | %Command Watt Limit | 0.1 | 40233 | USHORT

## SUN2000
State | Description | Factor | Register | Data Type | Remark
"use" | Active power | 0.001 | 32080 | SW_INT
"not use" | Active power adjustment | 1 | 40196 | SHORT
"not use" | Cabinet temperature | 0.1 | 32087 | SHORT
"not use" | Collect DSP data | 1 | 32002 | SHORT
"use" | Device status | 1 | 32089 | SHORT | 0x0000 Standby: initializing 0x0001 Standby: detecting insulation resistance 0x0002 Standby: detecting irradiation 0x0003 Standby: Grid detecting 0x0100 Starting 0x0200 On-grid 0x0201 Grid connection: power limited 0x0202 Grid connection: selfderating 0x0300 Shutdown: fault 0x0301 Shutdown: command 0x0302 Shutdown: OVGR 0x0303 Shutdown: communication disconnected 0x0304 Shutdown: power limited 0x0306 Shutdown: DC switches disconnected 0xA000 Standby: no irradiation
"use" | Energy yield of current day | 0.01 | 32114 | SW_UINT
"not use" | Grid frequency | 0.01 | 32085 | SHORT
"not use" | Input power | 0.001 | 32064 | SW_INT
"not use" | Locking | 1 | 40699 | SHORT
"not use" | Phase A current | 0.001 | 32072 | SW_INT
"not use" | Phase A voltage | 0.1 | 32069 | SHORT
"not use" | Phase B current | 0.001 | 32074 | SW_INT
"not use" | Phase B voltage | 0.1 | 32070 | SHORT
"not use" | Phase C current | 0.001 | 32076 | SW_INT
"not use" | Phase C voltage | 0.1 | 32071 | SHORT
"not use" | Power factor | 0.001 | 32084 | SHORT
"not use" | PV1 voltage | 0.1 | 32016 | SHORT
"not use" | PV1 current | 0.01 | 32017 | SHORT
"not use" | PV2 voltage | 0.1 | 32018 | SHORT
"not use" | PV2 current | 0.01 | 32019 | SHORT
"not use" | PV3 voltage | 0.1 | 32020 | SHORT
"not use" | PV3 current | 0.01 | 32021 | SHORT
"not use" | PV4 voltage | 0.1 | 32022 | SHORT
"not use" | PV4 current | 0.01 | 32023 | SHORT
"not use" | PV5 voltage | 0.1 | 32024 | SHORT
"not use" | PV5 current | 0.01 | 32025 | SHORT
"not use" | PV6 voltage | 0.1 | 32026 | SHORT
"not use" | PV6 current | 0.01 | 32027 | SHORT
"not use" | PV7 voltage | 0.1 | 32028 | SHORT
"not use" | PV7 current | 0.01 | 32029 | SHORT
"not use" | PV8 voltage | 0.1 | 32030 | SHORT
"not use" | PV8 current | 0.01 | 32031 | SHORT
"not use" | PV9 voltage | 0.1 | 32032 | SHORT
"not use" | PV9 current | 0.01 | 32033 | SHORT
"not use" | PV10 voltage | 0.1 | 32034 | SHORT
"not use" | PV10 current | 0.01 | 32035 | SHORT
"not use" | PV11 voltage | 0.1 | 32036 | SHORT
"not use" | PV11 current | 0.01 | 32037 | SHORT
"not use" | PV12 voltage | 0.1 | 32038 | SHORT
"not use" | PV12 current | 0.01 | 32039 | SHORT
"not use" | PV13 voltage | 0.1 | 32040 | SHORT
"not use" | PV13 current | 0.01 | 32041 | SHORT
"not use" | PV14 voltage | 0.1 | 32042 | SHORT
"not use" | PV14 current | 0.01 | 32043 | SHORT
"not use" | PV15 voltage | 0.1 | 32044 | SHORT
"not use" | PV15 current | 0.01 | 32045 | SHORT
"not use" | PV16 voltage | 0.1 | 32046 | SHORT
"not use" | PV16 current | 0.01 | 32047 | SHORT
"not use" | PV17 voltage | 0.1 | 32048 | SHORT
"not use" | PV17 current | 0.01 | 32049 | SHORT
"not use" | PV18 voltage | 0.1 | 32050 | SHORT
"not use" | PV18 current | 0.01 | 32051 | SHORT
"not use" | PV19 voltage | 0.1 | 32052 | SHORT
"not use" | PV19 current | 0.01 | 32053 | SHORT
"not use" | PV20 voltage | 0.1 | 32054 | SHORT
"not use" | PV20 current | 0.01 | 32055 | SHORT
"not use" | Rated power | 0.001 | 30073 | SHORT
"not use" | Reactive power | 0.001 | 32082 | SW_INT
"not use" | Reactive power adjustment | 1 | 40196 | SHORT
"not use" | Reduced CO2 emission | 0.1 | 43524 | SHORT
"not use" | Shutdown time | 1 | 32093 | USHORT
"not use" | Startup time | 1 | 32091 | USHORT
"not use" | Total energy yield | 0.01 | 32106 | SW_UINT
"not use" | Line Voltage L1-L2 | 0.1 | 32066 | SHORT
"not use" | Line Voltage L2-L3 | 0.1 | 32067 | SHORT
"not use" | Line Voltage L3-L1 | 0.1 | 32068 | SHORT
"not use" | Efficiency | 0.0001 | 32086 | SHORT
"not use" | Alarm_1 | 1 | 32008 | SHORT
"not use" | Alarm_2 | 1 | 32009 | SHORT
"not use" | Alarm_3 | 1 | 32010 | SHORT
"use" | Power_adjustment | 0.1 | 35302 | SHORT

## Weather Sensor
State | Description | Factor | Register | Data Type | Remark
"use" | Total_irradiation | 0.1 | 40035 | SHORT
"use" | Daily irradiation amount | 0.1 | 40043 | SW_INT
"use" | Total_irradiation_POA | 0.1 | 40038 | SHORT
"use" | Daily_irradiation_amount_POA | 1 | 40045 | SW_INT

## From LCD
0000FFFE | A | 0000 | Reg 0000FFFE | Reg 0000FFFE'
0000F010 | A | 090 | Current Date | 090 Current Date'
0000F011 | A | 091 | Current Time | 091 Current Time'
0000FC00 | A | 095 | D/TLast reset | 095D/TLast reset'
0000F032 | A | 096 | No. of reset | 096 No. of reset'
0000E033 | A | 093 | Inst. kW | 093 Inst. kW'
0000E043 | A | 193 | Inst. kVAr | 193 Inst. kVAr'
00000069 | A | 000 | 000 Total kWh | '000 Total kWh'
00000060 | A | 001 | kWh Rate A | 001 kWh Rate A'
00000061 | A | 002 | kWh Rate B | 002 kWh Rate B'
00000062 | A | 003 | kWh Rate C | 003 kWh Rate C'
00001000 | A | 005 | Max kW A | 005 Max kW A'
00001001 | A | 006 | Max kW B | 006 Max kW B'
00001002 | A | 007 | Max kW C | 007 Max kW C'
00001040 | A | 015 | kW-Cum A | 015 kW-Cum A '
00001041 | A | 016 | kW-Cum B | 016 kW-Cum B '
00001042 | A | 017 | kW-Cum C | 017 kW-Cum C'
00000169 | A | 100 | Total kVArh | 100 Total kVArh'
00000160 | A | 101 | kVArh A | 101 kVArh A'
00000161 | A | 102 | kVArh B | 102 kVArh B'
00000162 | A | 103 | kVArh C | 103 kVArh C'
00001100 | A | 105 | Max kVAr A | 105 Max kVAr A'
00001101 | A | 106 | Max kVAr B | 106 Max kVAr B'
00001102 | A | 107 | Max kVAr C | 107 Max kVAr C'
00001140 | A | 115 | kVAr-Cum A | 115 kVAr-Cum A '
00001141 | A | 116 | kVAr-Cum B | 116 kVAr-Cum B'
00001142 | A | 117 | kVAr-Cum C | 117 kVAr-Cum C'
0000F540 | B |  | CT Ratio | CT Ratio'
0000F541 | B |  | VT Ratio | VT Ratio'
0000F00A | B |  | Measurement Meth | Measurement Meth'
0000F500 | B |  | ABC_V+ABC_A | ABC_V+ABC_A'
0000E020 | B |  | V I Angle PhA | V I Angle PhA'
0000E021 | B |  | V I Angle PhB | V I Angle PhB'
0000E022 | B |  | V I Angle PhC | V I Angle PhC'
0000E026 | B |  | Power Factor | Power Factor'
0000E060 | B |  | Frequency | Frequency'
0000FC20 | B | 192 | LastPowerDown | 192LastPowerDown'
0000F093 | B | 292 | Last Power Up | 292Last Power Up'
0000FFFE | C | 0000 | Reg 0000FFFE | Reg 0000FFFE'
0000F010 | C | 090 | Current Date | 090 Current Date'
0000F011 | C | 091 | Current Time | 091 Current Time'
0000FC00 | C | 095 | D/T Last rese | 095D/T Last rese'
0000F032 | C | 096 | No. of Reset | 096 No. of Reset'
00000049 | C | 111 | BT Total kWh | 111 BT Total kWh'
00000040 | C | 010 | 010 BT kWh A | '010 BT kWh A'
00000041 | C | 020 | BT kWh B | 020 BT kWh B'
00000042 | C | 030 | 030 BT kWh C | '030 BT kWh C'
00001020 | C | 050 | PV kW A | 050 PV kW A'
00001021 | C | 060 | PV kW B | 060 PV kW B'
00001022 | C | 070 | PV kW C | 070 PV kW C'
00001040 | C | 015 | kW-Cum A | 015 kW-Cum A'
00001041 | C | 016 | kW-Cum B | 016 kW-Cum B'
00001042 | C | 017 | kW-Cum C | 017 kW-Cum C'
00000149 | C | 222 | BTTotal kVArh | 222BTTotal kVArh'
00001129 | C | 280 | PV kVAr | 280 PV kVAr'
00001149 | C | 118 | kVAr-Cum | 118 kVAr-Cum'
0000F016 | B |  | Current Status F | Current Status F'
0000F017 | B |  | Latched Status F | Latched Status F'

## Bill Point
ID | Previous value displayed in Section C | Register | AI
888 | Previous LCD Checking |  |  | 0000FFFE
90 | Previous DD-MM-YY of Reading | 0000F010 |  | 0000F010
91 | Previous Time of Reading | 0000F011 |  | 0000F011
95 | Previous DD-MM-YY : Time of Reset | 0000FC00 |  | 0000FC00
96 | PreviousTimes of Reset | 0000F032 |  | 0000F032
111 | Previous kWh Total Reading(Reset) | 00000049 |  | 00000049
10 | Previous kWh Rate A Reading(Reset) | 00000040 |  | 00000040
20 | Previous kWh Rate B Reading(Reset) | 00000041 |  | 00000041
30 | Previous kWh Rate C Reading(Reset) | 00000042 |  | 00000042
50 | Previous kWp Rate A Reading(Reset) | 00001020 |  | 00001020
60 | Previous kWp Rate B Reading(Reset) | 00001021 |  | 00001021
70 | Previous kWp Rate C Reading(Reset) | 00001022 |  | 00001022
15 | Previous Comulative kWh-Rate A Reading | 00001040 |  | 00001040
16 | Previous Comulative kWh-Rate B Reading | 00001041 |  | 00001041
17 | Previous Comulative kWh-Rate C Reading | 00001042 |  | 00001042
222 | Previous total of kVarh total Reading(Reset) | 00000149 |  | 00000149
280 | Previous kVar demand Total Reading(Reset) | 00001129 |  | 00001129
118 | Previous Comulative kVarh demand Total Reading(Reset) | 00001149 |  | 00001149

## VISTEC12 (2)
VT1 | VT2 | VT3 | MODBUS VISTEC1&2&KVIS | [5 empty] | ENOS KVIS | [11 empty] | ENOS VISTEC
Used | Used | Used | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Used | Used | Used | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Used | Used | Used | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT
Used | Used | Used | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT
Used | Used | Used | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT
Used | Used | Used | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT
0 | 0 | 0 | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT
0 | 0 | 0 | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT
0 | 0 | 0 | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT
0 | 0 | 0 | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT
0 | 0 | 0 | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT
0 | 0 | 0 | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT
Used | Used | Used | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT
0 | 0 | 0 | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT
0 | 0 | 0 | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT
0 | 0 | 0 | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT
0 | 0 | 0 | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT
0 | 0 | 0 | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT
0 | 0 | 0 | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT
0 | 0 | 0 | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT
0 | 0 | 0 | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT
0 | 0 | 0 | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT
Used | Used | Used | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 | Used | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT | 7044 | Used | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT
Used | Used | Used | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 | Used | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT | 7046 | Used | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT
Used | Used | Used | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 | Used | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT | 7048 | Used | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT
Used | Used | Used | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 | Used | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT | 7050 | Used | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT
0 | 0 | 0 | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT
0 | 0 | 0 | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT
0 | 0 | 0 | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT
Used | Used | Used | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 | Used | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT | 7058 | Used | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT
Used | Used | Used | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 | Used | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT | 7060 | Used | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT
Used | Used | Used | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 | Used | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT | 7062 | Used | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT
Used | Used | Used | 7065 | 00000149 | Ex BT Total kVA | 7064 | 7064 | Used | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT | 7064 | Used | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT
0 | 0 | 0 | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT
0 | 0 | 0 | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT
0 | 0 | 0 | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
0 | 0 | 0 | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
0 | 0 | 0 | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
0 | 0 | 0 | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
0 | 0 | 0 | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
0 | 0 | 0 | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
0 | 0 | 0 | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
0 | 0 | 0 | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
0 | 0 | 0 | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
0 | 0 | 0 | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
0 | 0 | 0 | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
0 | 0 | 0 | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
0 | 0 | 0 | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
0 | 0 | 0 | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
0 | 0 | 0 | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
0 | 0 | 0 | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
0 | 0 | 0 | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
0 | 0 | 0 | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
0 | 0 | 0 | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
0 | 0 | 0 | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
0 | 0 | 0 | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
0 | 0 | 0 | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Used | Used | Used | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT
Used | Used | Used | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT
Used | Used | Used | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT
0 | 0 | 0 | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT
0 | 0 | 0 | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT
0 | 0 | 0 | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT
Used | Used | Used | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT
0 | 0 | 0 | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT
0 | 0 | 0 | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT
0 | 0 | 0 | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT
0 | 0 | 0 | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT
0 | 0 | 0 | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT
0 | 0 | 0 | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT
0 | 0 | 0 | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT
0 | 0 | 0 | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT
0 | 0 | 0 | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT
0 | 0 | 0 | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT
0 | 0 | 0 | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT
0 | 0 | 0 | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT
0 | 0 | 0 | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT
0 | 0 | 0 | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT
0 | 0 | 0 | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT
0 | 0 | 0 | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT
0 | 0 | 0 | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT
0 | 0 | 0 | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT
0 | 0 | 0 | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT
0 | 0 | 0 | 7167 | 00000149 | Im BT Total kVA | 7166 | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT
0 | 0 | 0 | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT
0 | 0 | 0 | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT
#N/A | #N/A | #N/A | 7173 | 00000269 | Im Total kWh | 7172 | 7052 | Used | Peak Active power A | 86 | float | AI | 0.001 | 0 | Peak Active power A | 7052 | 3 | FLOAT | 7052 | Used | Peak Active power A | 86 | float | AI | 0.001 | 0 | Peak Active power A | 7052 | 3 | FLOAT
Used | Used | Used | 7175 | 00001129 | Ex PV KVarh | 7174 | 7054 | Used | Peak Active power B | 87 | float | AI | 0.001 | 0 | Peak Active power B | 7054 | 3 | FLOAT | 7054 | Used | Peak Active power B | 87 | float | AI | 0.001 | 0 | Peak Active power B | 7054 | 3 | FLOAT
#N/A | #N/A | #N/A | 7177 | 00008129 | Ex PV KVarh Tim | 7176 | 7056 | Used | Peak Active power C | 88 | float | AI | 0.001 | 0 | Peak Active power C | 7056 | 3 | FLOAT | 7056 | Used | Peak Active power C | 88 | float | AI | 0.001 | 0 | Peak Active power C | 7056 | 3 | FLOAT
Used | Used | Used | 7181 | 00001149 | Ex Total kVAr | 7180 | 7174 | Used | Peak Reactive Power | 89 | float | AI | 0.001 | 0 | Peak Reactive Power | 7174 | 3 | FLOAT | 7174 | Used | Peak Reactive Power | 89 | float | AI | 0.001 | 0 | Peak Reactive Power | 7174 | 3 | FLOAT
Used | Used | Used | 7183 | 0000F032 | NB Reset | 7182 | 7180 | Used | Ex_Total_kVAr | 90 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT | 7180 | Used | Ex_Total_kVAr | 90 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
#N/A | #N/A | #N/A | 7185 | 00008020 | Ex PV kW A Time | 7184 | 7182 | Used | No_of_Reset | 91 | float | AI | 1 | 0 | No_of_Reset | 7182 | 3 | SHORT | 7182 | Used | No_of_Reset | 91 | float | AI | 1 | 0 | No_of_Reset | 7182 | 3 | SHORT
#N/A | #N/A | #N/A | 7189 | 00008021 | Ex PV kW B Time | 7188
#N/A | #N/A | #N/A | 7193 | 00008022 | Ex PV kW C Time | 7192
#N/A | #N/A | #N/A | 7197 | 0000FC00 | DT of Reset | 7196
#N/A | #N/A | #N/A | 7201 | 0000F002 | Serial No | 7200

## VISTEC12
VT1 | VT2 | KVIS |  | MODBUS VISTEC1&2&KVIS | [5 empty] | ENOS KVIS | [11 empty] | ENOS VISTEC
Inst_kW | Inst_kW | Inst_kW | 0 | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Inst_kVAr | Inst_kVAr | Inst_kVAr | 1 | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Ex_Total_kWh | Ex_Total_kWh | Ex_Total_kWh | 2 | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT
Ex_kWh_RateA | Ex_kWh_RateA | Ex_kWh_RateA | 3 | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT
Ex_kWh_RateB | Ex_kWh_RateB | Ex_kWh_RateB | 4 | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT
Ex_kWh_RateC | Ex_kWh_RateC | Ex_kWh_RateC | 5 | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT
Ex_Total_kVArh | Ex_Total_kVArh | Ex_Total_kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT
Ex_BT_Total_kWh | Ex_BT_Total_kWh | Ex_BT_Total_kWh | 22 | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 | Used | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT | 7044 | Used | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT
Ex_BT_kWhA | Ex_BT_kWhA | Ex_BT_kWhA | 23 | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 | Used | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT | 7046 | Used | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT
Ex_BT_kWhB | Ex_BT_kWhB | Ex_BT_kWhB | 24 | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 | Used | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT | 7048 | Used | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT
Ex_BT_kWhC | Ex_BT_kWhC | Ex_BT_kWhC | 25 | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 | Used | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT | 7050 | Used | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT
Ex_kW_Cum_A2 | Ex_kW_Cum_A2 | Ex_kW_Cum_A2 | 29 | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 | Used | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT | 7058 | Used | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT
Ex_kW_Cum_B2 | Ex_kW_Cum_B2 | Ex_kW_Cum_B2 | 30 | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 | Used | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT | 7060 | Used | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT
Ex_kW_Cum_C2 | Ex_kW_Cum_C2 | Ex_kW_Cum_C2 | 31 | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 | Used | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT | 7062 | Used | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT
Ex_BT_Total_kVAr | Ex_BT_Total_kVAr | Ex_BT_Total_kVAr | 32 | 7065 | 00000149 | Ex BT Total kVA | 7064 | 7064 | Used | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT | 7064 | Used | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Im_kWh_RateA | Im_kWh_RateA | Im_kWh_RateA | 57 | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT
Im_kWh_RateB | Im_kWh_RateB | Im_kWh_RateB | 58 | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT
Im_kWh_RateC | Im_kWh_RateC | Im_kWh_RateC | 59 | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT
Im_Total_kVArh | Im_Total_kVArh | Im_Total_kVArh | 63 | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7167 | 00000149 | Im BT Total kVA | 7166 | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT
FALSE | FALSE | FALSE | FALSE | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT
#N/A | #N/A | #N/A | #N/A | 7173 | 00000269 | Im Total kWh | 7172 | 7052 | Used | Peak Active power A | 86 | float | AI | 0.001 | 0 | Peak Active power A | 7052 | 3 | FLOAT | 7052 | Used | Peak Active power A | 86 | float | AI | 0.001 | 0 | Peak Active power A | 7052 | 3 | FLOAT
Peak Reactive Power | Peak Reactive Power | Peak Reactive Power | 89 | 7175 | 00001129 | Ex PV KVarh | 7174 | 7054 | Used | Peak Active power B | 87 | float | AI | 0.001 | 0 | Peak Active power B | 7054 | 3 | FLOAT | 7054 | Used | Peak Active power B | 87 | float | AI | 0.001 | 0 | Peak Active power B | 7054 | 3 | FLOAT
#N/A | #N/A | #N/A | #N/A | 7177 | 00008129 | Ex PV KVarh Tim | 7176 | 7056 | Used | Peak Active power C | 88 | float | AI | 0.001 | 0 | Peak Active power C | 7056 | 3 | FLOAT | 7056 | Used | Peak Active power C | 88 | float | AI | 0.001 | 0 | Peak Active power C | 7056 | 3 | FLOAT
Ex_Total_kVAr | Ex_Total_kVAr | Ex_Total_kVAr | 90 | 7181 | 00001149 | Ex Total kVAr | 7180 | 7174 | Used | Peak Reactive Power | 89 | float | AI | 0.001 | 0 | Peak Reactive Power | 7174 | 3 | FLOAT | 7174 | Used | Peak Reactive Power | 89 | float | AI | 0.001 | 0 | Peak Reactive Power | 7174 | 3 | FLOAT
No_of_Reset | No_of_Reset | No_of_Reset | 91 | 7183 | 0000F032 | NB Reset | 7182 | 7180 | Used | Ex_Total_kVAr | 90 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT | 7180 | Used | Ex_Total_kVAr | 90 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
#N/A | #N/A | #N/A | #N/A | 7185 | 00008020 | Ex PV kW A Time | 7184 | 7182 | Used | No_of_Reset | 91 | float | AI | 1 | 0 | No_of_Reset | 7182 | 3 | SHORT | 7182 | Used | No_of_Reset | 91 | float | AI | 1 | 0 | No_of_Reset | 7182 | 3 | SHORT
#N/A | #N/A | #N/A | #N/A | 7189 | 00008021 | Ex PV kW B Time | 7188
#N/A | #N/A | #N/A | #N/A | 7193 | 00008022 | Ex PV kW C Time | 7192
#N/A | #N/A | #N/A | #N/A | 7197 | 0000FC00 | DT of Reset | 7196
#N/A | #N/A | #N/A | #N/A | 7201 | 0000F002 | Serial No | 7200

## TOP1
Check |  | METER |  |  |  | Enos
Inst_kW | 0 | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Inst_kVAr | 1 | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Ex_Total_kWh | 2 | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT
Ex_kWh_RateA | 3 | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT
Ex_kWh_RateB | 4 | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT
Ex_kWh_RateC | 5 | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT
FALSE | FALSE | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT
FALSE | FALSE | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT
FALSE | FALSE | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT
FALSE | FALSE | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT
FALSE | FALSE | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT
FALSE | FALSE | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT
Ex_Total_kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT
FALSE | FALSE | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT
FALSE | FALSE | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT
FALSE | FALSE | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT
FALSE | FALSE | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT
FALSE | FALSE | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT
FALSE | FALSE | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT
FALSE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT
FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT
FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT
FALSE | FALSE | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 |  | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT
FALSE | FALSE | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 |  | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT
FALSE | FALSE | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 |  | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT
FALSE | FALSE | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 |  | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT
FALSE | FALSE | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT
FALSE | FALSE | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT
FALSE | FALSE | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT
FALSE | FALSE | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 |  | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT
FALSE | FALSE | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 |  | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT
FALSE | FALSE | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 |  | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT
FALSE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | 7064 | 7064 |  | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT
FALSE | FALSE | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT
FALSE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT
FALSE | FALSE | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
FALSE | FALSE | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
FALSE | FALSE | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
FALSE | FALSE | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
FALSE | FALSE | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
FALSE | FALSE | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
FALSE | FALSE | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
FALSE | FALSE | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
FALSE | FALSE | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
FALSE | FALSE | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
FALSE | FALSE | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
FALSE | FALSE | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
FALSE | FALSE | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
FALSE | FALSE | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
FALSE | FALSE | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
FALSE | FALSE | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
FALSE | FALSE | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
FALSE | FALSE | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
FALSE | FALSE | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
FALSE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
FALSE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
FALSE | FALSE | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Im_kWh_RateA | 57 | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT
Im_kWh_RateB | 58 | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT
Im_kWh_RateC | 59 | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT
FALSE | FALSE | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT
FALSE | FALSE | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT
FALSE | FALSE | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT
Im_Total_kVArh | 63 | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT
FALSE | FALSE | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT
FALSE | FALSE | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT
FALSE | FALSE | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT
FALSE | FALSE | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT
FALSE | FALSE | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT
FALSE | FALSE | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT
FALSE | FALSE | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT
FALSE | FALSE | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT
FALSE | FALSE | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT
FALSE | FALSE | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT
FALSE | FALSE | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT
FALSE | FALSE | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT
FALSE | FALSE | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT
FALSE | FALSE | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT
FALSE | FALSE | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT
FALSE | FALSE | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT
FALSE | FALSE | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT
FALSE | FALSE | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT
FALSE | FALSE | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT
FALSE | FALSE | 7167 | 00000149 | Im BT Total kVArh | 7166 | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT
FALSE | FALSE | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT
FALSE | FALSE | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT
#N/A | #N/A | 7173 | 00000269 | Im Total kWh | 7172 | 7052 | Used | Peak Active power A | 86 | float | AI | 0.001 | 0 | Peak Active power A | 7052 | 3 | FLOAT
Peak Reactive Power | 89 | 7175 | 00001129 | Ex PV KVarh | 7174 | 7054 | Used | Peak Active power B | 87 | float | AI | 0.001 | 0 | Peak Active power B | 7054 | 3 | FLOAT
#N/A | #N/A | 7177 | 00008129 | Ex PV KVarh Time | 7176 | 7056 | Used | Peak Active power C | 88 | float | AI | 0.001 | 0 | Peak Active power C | 7056 | 3 | FLOAT
| FALSE | 7181 | 00001149 | Ex Total kVAr | 7180 | 7174 | Used | Peak Reactive Power | 89 | float | AI | 0.001 | 0 | Peak Reactive Power | 7174 | 3 | FLOAT
FALSE | FALSE | 7183 | 0000F032 | NB Reset | 7182 | 7180 |  | Ex_Total_kVAr | 90 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
#N/A | #N/A | 7185 | 00008020 | Ex PV kW A Time | 7184 | 7182 |  | No_of_Reset | 91 | float | AI | 1 | 0 | No_of_Reset | 7182 | 3 | SHORT
#N/A | #N/A | 7189 | 00008021 | Ex PV kW B Time | 7188 | 7186 |  | Peak_Time_A_1 | 92 | float | AI | 1 | 0 | Peak_Time_A_1 | 7186 | 3 | DOUBLE
#N/A | #N/A | 7193 | 00008022 | Ex PV kW C Time | 7192

## TOP2
Check |  | METER |  |  |  | Enos
Inst_kW | 0 | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Inst_kVAr | 1 | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Ex_Total_kWh | 2 | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT
Ex_kWh_RateA | 3 | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT
Ex_kWh_RateB | 4 | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT
Ex_kWh_RateC | 5 | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT
FALSE | FALSE | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT
FALSE | FALSE | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT
FALSE | FALSE | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT
FALSE | FALSE | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT
FALSE | FALSE | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT
FALSE | FALSE | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT
Ex_Total_kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT
FALSE | FALSE | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT
FALSE | FALSE | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT
FALSE | FALSE | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT
FALSE | FALSE | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT
FALSE | FALSE | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT
FALSE | FALSE | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT
FALSE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT
FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT
FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT
FALSE | FALSE | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 |  | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT
FALSE | FALSE | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 |  | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT
FALSE | FALSE | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 |  | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT
FALSE | FALSE | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 |  | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT
FALSE | FALSE | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT
FALSE | FALSE | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT
FALSE | FALSE | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT
FALSE | FALSE | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 |  | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT
FALSE | FALSE | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 |  | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT
FALSE | FALSE | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 |  | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT
FALSE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | 7064 | 7064 |  | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT
FALSE | FALSE | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT
FALSE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT
FALSE | FALSE | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
FALSE | FALSE | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
FALSE | FALSE | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
FALSE | FALSE | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
FALSE | FALSE | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
FALSE | FALSE | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
FALSE | FALSE | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
FALSE | FALSE | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
FALSE | FALSE | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
FALSE | FALSE | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
FALSE | FALSE | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
FALSE | FALSE | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
FALSE | FALSE | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
FALSE | FALSE | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
FALSE | FALSE | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
FALSE | FALSE | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
FALSE | FALSE | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
FALSE | FALSE | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
FALSE | FALSE | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
FALSE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
FALSE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
FALSE | FALSE | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Im_kWh_RateA | 57 | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT
Im_kWh_RateB | 58 | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT
Im_kWh_RateC | 59 | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT
FALSE | FALSE | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT
FALSE | FALSE | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT
FALSE | FALSE | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT
Im_Total_kVArh | 63 | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT
FALSE | FALSE | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT
FALSE | FALSE | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT
FALSE | FALSE | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT
FALSE | FALSE | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT
FALSE | FALSE | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT
FALSE | FALSE | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT
FALSE | FALSE | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT
FALSE | FALSE | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT
FALSE | FALSE | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT
FALSE | FALSE | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT
FALSE | FALSE | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT
FALSE | FALSE | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT
FALSE | FALSE | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT
FALSE | FALSE | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT
FALSE | FALSE | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT
FALSE | FALSE | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT
FALSE | FALSE | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT
FALSE | FALSE | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT
FALSE | FALSE | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT
FALSE | FALSE | 7167 | 00001349 | Im BT Total kVAr | 7166 | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT
FALSE | FALSE | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT
FALSE | FALSE | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT
#N/A | #N/A | 7173 | 00000269 | Im Total kWh | 7172 | 7052 | Used | Peak Active power A | 86 | float | AI | 0.001 | 0 | Peak Active power A | 7052 | 3 | FLOAT
Peak Reactive Power | 89 | 7175 | 00001129 | Ex PV KVarh | 7174 | 7054 | Used | Peak Active power B | 87 | float | AI | 0.001 | 0 | Peak Active power B | 7054 | 3 | FLOAT
#N/A | #N/A | 7177 | 00001129 | Ex PV KVarh | 7176 | 7056 | Used | Peak Active power C | 88 | float | AI | 0.001 | 0 | Peak Active power C | 7056 | 3 | FLOAT
#N/A | #N/A | 7179 | 00008129 | Ex PV KVarh Time | 7178 | 7174 | Used | Peak Reactive Power | 89 | float | AI | 0.001 | 0 | Peak Reactive Power | 7174 | 3 | FLOAT
FALSE | FALSE | 7181 | 00008129 | Ex PV KVarh Time | 7180 | 7180 |  | Ex_Total_kVAr | 90 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
FALSE | FALSE | 7183 | 00001149 | Ex Total kVAr | 7182 | 7182 |  | No_of_Reset | 91 | float | AI | 1 | 0 | No_of_Reset | 7182 | 3 | SHORT
#N/A | #N/A | 7185 | 0000F032 | NB Reset | 7184 | 7186 |  | Peak_Time_A_1 | 92 | float | AI | 1 | 0 | Peak_Time_A_1 | 7186 | 3 | DOUBLE
FALSE | FALSE | 7187 | 00008020 | Ex PV kW A Time | 7186
#N/A | #N/A | 7191 | 00008021 | Ex PV kW B Time | 7190
#N/A | #N/A | 7195 | 00008022 | Ex PV kW C Time | 7194
#N/A | #N/A | 7199 | 0000FC00 | DT of Reset | 7198

## PTTMRB
Check |  | METER |  |  |  | Enos
Ex Total kWh | 9 | 7001 | 00000069 | Ex Total kWh | 7000 | 7040 |  | A-B line voltage | 1 | float | AI | 1 | 0 | EMT.VolL1 | 7040 | 3 | FLOAT
Ex_kWh_RateA | 19 | 7003 | 00000060 | Ex kWh RateA | 7002 | 7042 |  | B-C line voltage | 2 | float | AI | 1 | 0 | EMT.VolL2 | 7042 | 3 | FLOAT
Ex_kWh_RateB | 20 | 7005 | 00000061 | Ex kWh RateB | 7004 | 7044 |  | C-A line voltage | 3 | float | AI | 1 | 0 | EMT.VolL3 | 7044 | 3 | FLOAT
Ex_kWh_RateC | 21 | 7007 | 00000062 | Ex kWh RateC | 7006 | 7046 | Used | Phase A current | 4 | float | AI | 1 | 0 | EMT.CurPh1 | 7046 | 3 | FLOAT
Peak Active power A | 15 | 7009 | 00001000 | Ex Max kW A | 7008 | 7048 | Used | Phase B current | 5 | float | AI | 1 | 0 | EMT.CurPh2 | 7048 | 3 | FLOAT
Peak Active power B | 16 | 7011 | 00001001 | Ex Max kW B | 7010 | 7050 | Used | Phase C current | 6 | float | AI | 1 | 0 | EMT.CurPh3 | 7050 | 3 | FLOAT
Peak Active power C | 17 | 7013 | 00001002 | Ex Max kW C | 7012 | 7058 |  | Frequency | 7 | float | AI | 1 | 0 | Frequency | 7058 | 3 | FLOAT
#N/A | #N/A | 7015 | 00001040 | Ex kW-Cum A | 7014 | 7060 | Used | Power Factor | 8 | float | AI | 1 | 0 | Power Factor | 7060 | 3 | FLOAT
#N/A | #N/A | 7017 | 00001041 | Ex kW-Cum B | 7016 | 7000 | Used | Ex Total kWh | 9 | float | AI | 0.001 | 0 | EMT.APProductionKWH | 7000 | 3 | FLOAT
#N/A | #N/A | 7019 | 00001042 | Ex kW-Cum C | 7018 | 7020 | Used | Ex Total kVArh | 10 | float | AI | 0.001 | 0 | EMT.RPProductionKWH | 7020 | 3 | FLOAT
Ex Total kVArh | 10 | 7021 | 00000169 | Ex Total kVArh | 7020 | 7114 | Used | Im Total kWh | 11 | float | AI | 0.001 | 0 | EMT.APConsumedKWH | 7114 | 3 | FLOAT
#N/A | #N/A | 7023 | 00000160 | Ex kVArh A | 7022 | 7116 | Used | Im Total kVArh | 12 | float | AI | 0.001 | 0 | EMT.RPConsumedKWH | 7116 | 3 | FLOAT
#N/A | #N/A | 7025 | 00000161 | Ex kVArh B | 7024 | 7118 | Used | Active Power | 13 | float | AI | 0.001 | 0 | EMT.ActivePW | 7118 | 3 | FLOAT
#N/A | #N/A | 7027 | 00000162 | Ex kVArh C | 7026 | 7120 | Used | Reactive Power | 14 | float | AI | 0.001 | 0 | EMT.ReactivePW | 7120 | 3 | FLOAT
#N/A | #N/A | 7029 | 00001100 | Ex Max kVAr A | 7028 | 7008 | Used | Peak Active power A | 15 | float | AI | 0.001 | 0 | Peak Active power A | 7008 | 3 | FLOAT
#N/A | #N/A | 7031 | 00001101 | Ex Max kVAr B | 7030 | 7010 | Used | Peak Active power B | 16 | float | AI | 0.001 | 0 | Peak Active power B | 7010 | 3 | FLOAT
#N/A | #N/A | 7033 | 00001102 | Ex Max kVAr C | 7032 | 7012 | Used | Peak Active power C | 17 | float | AI | 0.001 | 0 | Peak Active power C | 7012 | 3 | FLOAT
#N/A | #N/A | 7035 | 00000140 | Ex kVArh-Cum A | 7034 | 7138 | Used | Peak Reactive Power | 18 | float | AI | 0.001 | 0 | Peak Reactive Power | 7138 | 3 | FLOAT
#N/A | #N/A | 7037 | 00000141 | Ex kVArh-Cum B | 7036 | 7002 | Used | Ex_kWh_RateA | 19 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7002 | 3 | FLOAT
#N/A | #N/A | 7039 | 00000142 | Ex kVArh-Cum C | 7038 | 7004 | Used | Ex_kWh_RateB | 20 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7004 | 3 | FLOAT
FALSE | FALSE | 7041 | 0000E000 | Ph A Volt | 7040 | 7006 | Used | Ex_kWh_RateC | 21 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7006 | 3 | FLOAT
FALSE | FALSE | 7043 | 0000E001 | Ph B Volt | 7042
FALSE | FALSE | 7045 | 0000E002 | Ph C Volt | 7044
Phase A current | 4 | 7047 | 0000E010 | Ph A Curr | 7046
Phase B current | 5 | 7049 | 0000E011 | Ph B Curr | 7048
Phase C current | 6 | 7051 | 0000E012 | Ph C Curr | 7050
#N/A | #N/A | 7053 | 0000E020 | Ph A angle | 7052
#N/A | #N/A | 7055 | 0000E021 | Ph B angle | 7054
#N/A | #N/A | 7057 | 0000E022 | Ph C angle | 7056
FALSE | FALSE | 7059 | 0000E060 | Frequency | 7058
Power Factor | 8 | 7061 | 0000E026 | Power Factor | 7060
#N/A | #N/A | 7063 | 0000F03D | Current DateTime | 7062
#N/A | #N/A | 7069 | 0000FC00 | DT LastReset | 7068
#N/A | #N/A | 7075 | 0000F032 | No.of reset | 7074
#N/A | #N/A | 7077 | 0000F540 | CT ratio | 7076
#N/A | #N/A | 7079 | 0000F541 | VT ratio | 7078
#N/A | #N/A | 7081 | 0000FC20 | Last PowerDown | 7080
#N/A | #N/A | 7087 | 0000F093 | Last PowerUP | 7086
#N/A | #N/A | 7093 | 0000F016 | Current Alarm | 7092
#N/A | #N/A | 7101 | 0000F017 | Latched Alarm | 7100
Im Total kWh | 11 | 7115 | 00000269 | Ex Total kWh | 7114
Im Total kVArh | 12 | 7117 | 00000369 | Ex Total kWh | 7116
Active Power | 13 | 7119 | 0000E033 | Active power | 7118
Reactive Power | 14 | 7121 | 0000E043 | Reactive power | 7120
#N/A | #N/A | 7123 | 00000049 | Ex BT Total kWh | 7122
#N/A | #N/A | 7125 | 00000040 | Ex BT kWh Rate A | 7124
#N/A | #N/A | 7127 | 00000041 | Ex BT kWh Rate B | 7126
#N/A | #N/A | 7129 | 00000042 | Ex BT kWh Rate C | 7128
#N/A | #N/A | 7131 | 00001020 | Ex PV kWh C | 7130
#N/A | #N/A | 7133 | 00001021 | Ex PV kWh B | 7132
#N/A | #N/A | 7135 | 00001022 | Ex PV kWh C | 7134
#N/A | #N/A | 7137 | 00000149 | Ex BT Total kVAr | 7136
Peak Reactive Power | 18 | 7139 | 00001129 | Ex PV KVarh | 7138
#N/A | #N/A | 7141 | 00001149 | Ex Total kVAr | 7140
#N/A | #N/A | 7143 | 00008020 | Ex PV kWp A Time | 7142
#N/A | #N/A | 7147 | 00008021 | Ex PV kWp B Time | 7146
#N/A | #N/A | 7151 | 00008022 | Ex PV kWp C Time | 7150

## AICA
Check |  | METER |  |  |  | Enos
Inst_kW | 0 | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Inst_kVAr | 1 | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Ex_Total_kWh | 2 | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT
Ex_kWh_RateA | 3 | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT
Ex_kWh_RateB | 4 | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT
Ex_kWh_RateC | 5 | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT
FALSE | FALSE | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT
FALSE | FALSE | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT
FALSE | FALSE | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT
FALSE | FALSE | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT
FALSE | FALSE | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT
FALSE | FALSE | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT
Ex_Total_kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT
FALSE | FALSE | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT
FALSE | FALSE | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT
FALSE | FALSE | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT
FALSE | FALSE | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT
FALSE | FALSE | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT
FALSE | FALSE | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT
FALSE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT
FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT
FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT
Ex_BT_Total_kWh | 22 | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 | Used | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT
Ex_BT_kWhA | 23 | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 | Used | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT
Ex_BT_kWhB | 24 | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 | Used | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT
Ex_BT_kWhC | 25 | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 | Used | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT
FALSE | FALSE | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT
FALSE | FALSE | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT
FALSE | FALSE | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT
FALSE | FALSE | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 |  | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT
FALSE | FALSE | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 |  | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT
FALSE | FALSE | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 |  | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT
FALSE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | 7064 | 7064 |  | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT
FALSE | FALSE | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT
FALSE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT
Ph_A_Volt | 35 | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 | Used | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
Ph_B_Volt | 36 | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 | Used | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
Ph_C_Volt | 37 | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 | Used | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
Ph_A_Curr | 38 | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 | Used | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
Ph_B_Curr | 39 | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 | Used | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
Ph_C_Curr | 40 | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 | Used | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
FALSE | FALSE | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
FALSE | FALSE | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
FALSE | FALSE | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
FALSE | FALSE | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
FALSE | FALSE | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
FALSE | FALSE | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
FALSE | FALSE | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
FALSE | FALSE | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
FALSE | FALSE | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
FALSE | FALSE | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
FALSE | FALSE | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
FALSE | FALSE | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
FALSE | FALSE | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
FALSE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
FALSE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
FALSE | FALSE | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Im_kWh_RateA | 57 | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT
Im_kWh_RateB | 58 | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT
Im_kWh_RateC | 59 | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT
FALSE | FALSE | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT
FALSE | FALSE | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT
FALSE | FALSE | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT
Im_Total_kVArh | 63 | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT
FALSE | FALSE | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT
FALSE | FALSE | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT
FALSE | FALSE | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT
FALSE | FALSE | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT
FALSE | FALSE | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT
FALSE | FALSE | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT
FALSE | FALSE | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT
FALSE | FALSE | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT
FALSE | FALSE | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT
FALSE | FALSE | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT
FALSE | FALSE | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT
FALSE | FALSE | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT
FALSE | FALSE | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT
FALSE | FALSE | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT
FALSE | FALSE | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT
FALSE | FALSE | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT
FALSE | FALSE | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT
FALSE | FALSE | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT
FALSE | FALSE | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT
FALSE | FALSE | 7167 | 00000149 | Im BT Total kVArh | 7166 | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT
FALSE | FALSE | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT
FALSE | FALSE | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT
Im_total_kWh | 86 | 7173 | 00000269 | Im Total kWh | 7172 | 7172 | Used | Im_total_kWh | 86 | float | AI | 0.001 | 0 | Im_total_kWh | 7172 | 3 | FLOAT
#N/A | #N/A | 7175 | 00001129 | Ex PV KVarh | 7174 | 7180 |  | Ex_Total_kVAr | 87 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
#N/A | #N/A | 7250 | 00008129 | Ex PV KVarh Time | 7249
FALSE | FALSE | 7181 | 00001149 | Ex Total kVAr | 7180
#N/A | #N/A | 7183 | 0000F032 | NB Reset | 7182
#N/A | #N/A | 7185 | 00008020 | Ex PV kW A Time | 7184
#N/A | #N/A | 7189 | 00008021 | Ex PV kW B Time | 7188
#N/A | #N/A | 7193 | 00008022 | Ex PV kW C Time | 7192
#N/A | #N/A | 7207 | 0000F092 | Check_LCD | 7206
#N/A | #N/A | 7209 | 0000F032 | Count_reset | 7208
#N/A | #N/A | 7300 | 0000F03D | Date_time | 7299
#N/A | #N/A | 7400 | 0000FC00 | Date_Reset_meter | 7399
|  | ModB | is using | rt for accessing slave | meters.

## SUT
Check |  | METER |  |  |  | Enos
Inst_kW | 0 | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Inst_kVAr | 1 | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Ex_Total_kWh | 2 | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT
Ex_kWh_RateA | 3 | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT
Ex_kWh_RateB | 4 | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT
Ex_kWh_RateC | 5 | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT
FALSE | FALSE | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT
FALSE | FALSE | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT
FALSE | FALSE | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT
FALSE | FALSE | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT
FALSE | FALSE | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT
FALSE | FALSE | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT
Ex_Total_kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT
FALSE | FALSE | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT
FALSE | FALSE | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT
FALSE | FALSE | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT
FALSE | FALSE | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT
FALSE | FALSE | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT
FALSE | FALSE | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT
FALSE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT
FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT
FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT
Ex_BT_Total_kWh | 22 | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 | Used | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT
Ex_BT_kWhA | 23 | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 | Used | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT
Ex_BT_kWhB | 24 | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 | Used | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT
Ex_BT_kWhC | 25 | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 | Used | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT
FALSE | FALSE | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT
FALSE | FALSE | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT
FALSE | FALSE | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT
FALSE | FALSE | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 |  | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT
FALSE | FALSE | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 |  | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT
FALSE | FALSE | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 |  | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT
FALSE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | 7064 | 7064 |  | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT
FALSE | FALSE | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT
FALSE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT
FALSE | FALSE | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
FALSE | FALSE | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
FALSE | FALSE | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
FALSE | FALSE | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
FALSE | FALSE | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
FALSE | FALSE | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
FALSE | FALSE | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
FALSE | FALSE | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
FALSE | FALSE | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
FALSE | FALSE | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
FALSE | FALSE | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
FALSE | FALSE | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
FALSE | FALSE | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
FALSE | FALSE | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
FALSE | FALSE | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
FALSE | FALSE | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
FALSE | FALSE | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
FALSE | FALSE | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
FALSE | FALSE | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
FALSE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
FALSE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
FALSE | FALSE | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Im_kWh_RateA | 57 | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT
Im_kWh_RateB | 58 | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT
Im_kWh_RateC | 59 | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT
FALSE | FALSE | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT
FALSE | FALSE | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT
FALSE | FALSE | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT
Im_Total_kVArh | 63 | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT
FALSE | FALSE | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT
FALSE | FALSE | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT
FALSE | FALSE | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT
FALSE | FALSE | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT
FALSE | FALSE | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT
FALSE | FALSE | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT
FALSE | FALSE | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT
FALSE | FALSE | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT
FALSE | FALSE | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT
FALSE | FALSE | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT
FALSE | FALSE | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT
FALSE | FALSE | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT
FALSE | FALSE | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT
FALSE | FALSE | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT
FALSE | FALSE | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT
FALSE | FALSE | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT
FALSE | FALSE | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT
FALSE | FALSE | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT
FALSE | FALSE | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT
FALSE | FALSE | 7167 | 00000149 | Im BT Total kVArh | 7166 | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT
FALSE | FALSE | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT
FALSE | FALSE | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT
Im_total_kWh | 86 | 7173 | 00000269 | Im Total kWh | 7172 | 7172 | Used | Im_total_kWh | 86 | float | AI | 0.001 | 0 | Im_total_kWh | 7172 | 3 | FLOAT
FALSE | FALSE | 7175 | 00001129 | Ex PV KVarh | 7174 | 7180 |  | Ex_Total_kVAr | 87 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
#N/A | #N/A | 7177 | 00008129 | Ex PV KVarh Time | 7176 | 7174 |  | Ex PV KVarh | 88 | float | AI | 0.001 | 0 | Ex PV KVarh | 7174 | 3 | FLOAT
FALSE | FALSE | 7181 | 00001149 | Ex Total kVAr | 7180 | 7182 |  | No_of_Reset | 89 | float | AI | 1 | 0 | No_of_Reset | 7182 | 3 | SHORT
FALSE | FALSE | 7183 | 0000F032 | NB Reset | 7182
#N/A | #N/A | 7185 | 00008020 | Ex PV kW A Time | 7184
#N/A | #N/A | 7189 | 00008021 | Ex PV kW B Time | 7188
#N/A | #N/A | 7193 | 00008022 | Ex PV kW C Time | 7192

## Suretex
Check |  | METER |  |  |  | Enos
Inst_kW | 0 | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Inst_kVAr | 1 | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Ex_Total_kWh | 2 | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT
Ex_kWh_RateA | 3 | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT
Ex_kWh_RateB | 4 | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT
Ex_kWh_RateC | 5 | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT
FALSE | FALSE | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT
FALSE | FALSE | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT
FALSE | FALSE | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT
FALSE | FALSE | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT
FALSE | FALSE | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT
FALSE | FALSE | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT
Ex_Total_kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT
FALSE | FALSE | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT
FALSE | FALSE | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT
FALSE | FALSE | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT
FALSE | FALSE | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT
FALSE | FALSE | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT
FALSE | FALSE | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT
FALSE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT
FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT
FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT
Ex_BT_Total_kWh | 22 | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 | Used | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT
Ex_BT_kWhA | 23 | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 | Used | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT
Ex_BT_kWhB | 24 | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 | Used | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT
Ex_BT_kWhC | 25 | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 | Used | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT
FALSE | FALSE | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT
FALSE | FALSE | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT
FALSE | FALSE | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT
FALSE | FALSE | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 |  | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT
FALSE | FALSE | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 |  | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT
FALSE | FALSE | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 |  | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT
FALSE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | 7064 | 7064 |  | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT
FALSE | FALSE | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT
FALSE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT
FALSE | FALSE | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
FALSE | FALSE | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
FALSE | FALSE | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
FALSE | FALSE | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
FALSE | FALSE | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
FALSE | FALSE | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
FALSE | FALSE | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
FALSE | FALSE | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
FALSE | FALSE | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
FALSE | FALSE | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
FALSE | FALSE | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
FALSE | FALSE | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
FALSE | FALSE | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
FALSE | FALSE | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
FALSE | FALSE | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
FALSE | FALSE | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
FALSE | FALSE | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
FALSE | FALSE | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
FALSE | FALSE | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
FALSE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
FALSE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
FALSE | FALSE | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Im_kWh_RateA | 57 | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT
Im_kWh_RateB | 58 | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT
Im_kWh_RateC | 59 | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT
FALSE | FALSE | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT
FALSE | FALSE | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT
FALSE | FALSE | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT
Im_Total_kVArh | 63 | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT
FALSE | FALSE | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT
FALSE | FALSE | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT
FALSE | FALSE | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT
FALSE | FALSE | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT
FALSE | FALSE | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT
FALSE | FALSE | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT
FALSE | FALSE | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT
FALSE | FALSE | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT
FALSE | FALSE | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT
FALSE | FALSE | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT
FALSE | FALSE | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT
FALSE | FALSE | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT
FALSE | FALSE | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT
FALSE | FALSE | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT
FALSE | FALSE | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT
FALSE | FALSE | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT
FALSE | FALSE | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT
FALSE | FALSE | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT
FALSE | FALSE | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT
FALSE | FALSE | 7167 | 00000149 | Im BT Total kVArh | 7166 | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT
FALSE | FALSE | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT
FALSE | FALSE | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT
Im_total_kWh | 86 | 7173 | 00000269 | Im Total kWh | 7172 | 7172 | Used | Im_total_kWh | 86 | float | AI | 0.001 | 0 | Im_total_kWh | 7172 | 3 | FLOAT
#N/A | #N/A | 7175 | 00001129 | Ex PV KVarh | 7174 | 7180 |  | Ex_Total_kVAr | 87 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
#N/A | #N/A | 7177 | 00008129 | Ex PV KVarh Time | 7176
| FALSE | 7181 | 00001149 | Ex Total kVAr | 7180
#N/A | #N/A | 7183 | 0000F032 | NB Reset | 7182
#N/A | #N/A | 7185 | 00008020 | Ex PV kW A Time | 7184
#N/A | #N/A | 7189 | 00008021 | Ex PV kW B Time | 7188
#N/A | #N/A | 7193 | 00008022 | Ex PV kW C Time | 7192

## PTIC
Check |  | METER |  |  |  | Enos
Inst_kW | 0 | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Inst_kVAr | 1 | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Ex_Total_kWh | 2 | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT
Ex_kWh_RateA | 3 | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT
Ex_kWh_RateB | 4 | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT
Ex_kWh_RateC | 5 | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT
FALSE | FALSE | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT
FALSE | FALSE | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT
FALSE | FALSE | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT
FALSE | FALSE | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT
FALSE | FALSE | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT
FALSE | FALSE | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT
Ex_Total_kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT
FALSE | FALSE | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT
FALSE | FALSE | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT
FALSE | FALSE | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT
FALSE | FALSE | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT
FALSE | FALSE | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT
FALSE | FALSE | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT
FALSE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT
FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT
FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT
Ex_BT_Total_kWh | 22 | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 | Used | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT
Ex_BT_kWhA | 23 | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 | Used | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT
Ex_BT_kWhB | 24 | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 | Used | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT
Ex_BT_kWhC | 25 | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 | Used | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT
FALSE | FALSE | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT
FALSE | FALSE | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT
FALSE | FALSE | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT
FALSE | FALSE | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 |  | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT
FALSE | FALSE | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 |  | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT
FALSE | FALSE | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 |  | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT
FALSE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | 7064 | 7064 |  | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT
FALSE | FALSE | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT
FALSE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT
FALSE | FALSE | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
FALSE | FALSE | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
FALSE | FALSE | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
FALSE | FALSE | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
FALSE | FALSE | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
FALSE | FALSE | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
FALSE | FALSE | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
FALSE | FALSE | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
FALSE | FALSE | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
FALSE | FALSE | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
FALSE | FALSE | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
FALSE | FALSE | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
FALSE | FALSE | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
FALSE | FALSE | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
FALSE | FALSE | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
FALSE | FALSE | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
FALSE | FALSE | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
FALSE | FALSE | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
FALSE | FALSE | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
FALSE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
FALSE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
FALSE | FALSE | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Im_kWh_RateA | 57 | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT
Im_kWh_RateB | 58 | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT
Im_kWh_RateC | 59 | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT
FALSE | FALSE | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT
FALSE | FALSE | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT
FALSE | FALSE | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT
Im_Total_kVArh | 63 | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT
FALSE | FALSE | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT
FALSE | FALSE | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT
FALSE | FALSE | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT
FALSE | FALSE | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT
FALSE | FALSE | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT
FALSE | FALSE | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT
FALSE | FALSE | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT
FALSE | FALSE | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT
FALSE | FALSE | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT
FALSE | FALSE | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT
FALSE | FALSE | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT
FALSE | FALSE | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT
FALSE | FALSE | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT
FALSE | FALSE | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT
FALSE | FALSE | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT
FALSE | FALSE | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT
FALSE | FALSE | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT
FALSE | FALSE | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT
FALSE | FALSE | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT
FALSE | FALSE | 7167 | 00000149 | Im BT Total kVArh | 7166 | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT
FALSE | FALSE | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT
FALSE | FALSE | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT
Im_total_kWh | 86 | 7173 | 00000269 | Im Total kWh | 7172 | 7172 | Used | Im_total_kWh | 86 | float | AI | 0.001 | 0 | Im_total_kWh | 7172 | 3 | FLOAT
#N/A | #N/A | 7175 | 00001129 | Ex PV KVarh | 7174 | 7180 |  | Ex_Total_kVAr | 87 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
#N/A | #N/A | 7177 | 00008129 | Ex PV KVarh Time | 7176
FALSE | FALSE | 7181 | 00001149 | Ex Total kVAr | 7180
#N/A | #N/A | 7183 | 0000F032 | NB Reset | 7182
#N/A | #N/A | 7185 | 00008020 | Ex PV kW A Time | 7184
#N/A | #N/A | 7189 | 00008021 | Ex PV kW B Time | 7188
#N/A | #N/A | 7193 | 00008022 | Ex PV kW C Time | 7192

## RASC
Check |  | METER |  |  |  | Enos
Inst_kW | 0 | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Inst_kVAr | 1 | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Ex_Total_kWh | 2 | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT
Ex_kWh_RateA | 3 | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT
Ex_kWh_RateB | 4 | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT
Ex_kWh_RateC | 5 | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT
FALSE | FALSE | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT
FALSE | FALSE | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT
FALSE | FALSE | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT
FALSE | FALSE | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT
FALSE | FALSE | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT
FALSE | FALSE | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT
Ex_Total_kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT
FALSE | FALSE | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT
FALSE | FALSE | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT
FALSE | FALSE | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT
FALSE | FALSE | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT
FALSE | FALSE | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT
FALSE | FALSE | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT
FALSE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT
FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT
FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT
Ex_BT_Total_kWh | 22 | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 | Used | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT
Ex_BT_kWhA | 23 | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 | Used | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT
Ex_BT_kWhB | 24 | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 | Used | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT
Ex_BT_kWhC | 25 | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 | Used | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT
FALSE | FALSE | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT
FALSE | FALSE | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT
FALSE | FALSE | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT
FALSE | FALSE | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 |  | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT
FALSE | FALSE | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 |  | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT
FALSE | FALSE | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 |  | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT
FALSE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | 7064 | 7064 |  | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT
FALSE | FALSE | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT
FALSE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT
FALSE | FALSE | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
FALSE | FALSE | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
FALSE | FALSE | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
FALSE | FALSE | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
FALSE | FALSE | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
FALSE | FALSE | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
FALSE | FALSE | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
FALSE | FALSE | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
FALSE | FALSE | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
FALSE | FALSE | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
FALSE | FALSE | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
FALSE | FALSE | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
FALSE | FALSE | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
FALSE | FALSE | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
FALSE | FALSE | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
FALSE | FALSE | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
FALSE | FALSE | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
FALSE | FALSE | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
FALSE | FALSE | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
FALSE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
FALSE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
FALSE | FALSE | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Im_kWh_RateA | 57 | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT
Im_kWh_RateB | 58 | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT
Im_kWh_RateC | 59 | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT
FALSE | FALSE | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT
FALSE | FALSE | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT
FALSE | FALSE | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT
Im_Total_kVArh | 63 | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT
FALSE | FALSE | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT
FALSE | FALSE | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT
FALSE | FALSE | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT
FALSE | FALSE | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT
FALSE | FALSE | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT
FALSE | FALSE | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT
FALSE | FALSE | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT
FALSE | FALSE | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT
FALSE | FALSE | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT
FALSE | FALSE | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT
FALSE | FALSE | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT
FALSE | FALSE | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT
FALSE | FALSE | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT
FALSE | FALSE | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT
FALSE | FALSE | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT
FALSE | FALSE | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT
FALSE | FALSE | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT
FALSE | FALSE | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT
FALSE | FALSE | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT
FALSE | FALSE | 7167 | 00000149 | Im BT Total kVArh | 7166 | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT
FALSE | FALSE | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT
FALSE | FALSE | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT
Im_total_kWh | 86 | 7173 | 00000269 | Im Total kWh | 7172 | 7172 | Used | Im_total_kWh | 86 | float | AI | 0.001 | 0 | Im_total_kWh | 7172 | 3 | FLOAT
#N/A | #N/A | 7175 | 00001129 | Ex PV KVarh | 7174 | 7180 |  | Ex_Total_kVAr | 87 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
#N/A | #N/A | 7177 | 00008129 | Ex PV KVarh Time | 7176
FALSE | FALSE | 7181 | 00001149 | Ex Total kVAr | 7180
#N/A | #N/A | 7183 | 0000F032 | NB Reset | 7182
#N/A | #N/A | 7185 | 00008020 | Ex PV kW A Time | 7184
#N/A | #N/A | 7189 | 00008021 | Ex PV kW B Time | 7188
#N/A | #N/A | 7193 | 00008022 | Ex PV kW C Time | 7192

## ENTER
Check |  | METER |  |  |  | Enos
Inst_kW | 0 | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Inst_kVAr | 1 | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Ex_Total_kWh | 2 | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT
Ex_kWh_RateA | 3 | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT
Ex_kWh_RateB | 4 | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT
Ex_kWh_RateC | 5 | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT
FALSE | FALSE | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT
FALSE | FALSE | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT
FALSE | FALSE | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT
FALSE | FALSE | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT
FALSE | FALSE | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT
FALSE | FALSE | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT
Ex_Total_kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT
FALSE | FALSE | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT
FALSE | FALSE | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT
FALSE | FALSE | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT
FALSE | FALSE | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT
FALSE | FALSE | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT
FALSE | FALSE | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT
FALSE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT
FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT
FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT
Ex_BT_Total_kWh | 22 | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 | Used | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT
Ex_BT_kWhA | 23 | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 | Used | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT
Ex_BT_kWhB | 24 | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 | Used | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT
Ex_BT_kWhC | 25 | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 | Used | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT
FALSE | FALSE | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT
FALSE | FALSE | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT
FALSE | FALSE | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT
FALSE | FALSE | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 |  | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT
FALSE | FALSE | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 |  | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT
FALSE | FALSE | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 |  | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT
FALSE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | 7064 | 7064 |  | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT
FALSE | FALSE | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT
FALSE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT
FALSE | FALSE | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
FALSE | FALSE | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
FALSE | FALSE | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
FALSE | FALSE | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
FALSE | FALSE | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
FALSE | FALSE | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
FALSE | FALSE | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
FALSE | FALSE | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
FALSE | FALSE | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
FALSE | FALSE | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
FALSE | FALSE | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
FALSE | FALSE | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
FALSE | FALSE | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
FALSE | FALSE | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
FALSE | FALSE | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
FALSE | FALSE | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
FALSE | FALSE | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
FALSE | FALSE | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
FALSE | FALSE | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
FALSE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
FALSE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
FALSE | FALSE | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Im_kWh_RateA | 57 | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT
Im_kWh_RateB | 58 | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT
Im_kWh_RateC | 59 | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT
FALSE | FALSE | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT
FALSE | FALSE | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT
FALSE | FALSE | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT
Im_Total_kVArh | 63 | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT
FALSE | FALSE | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT
FALSE | FALSE | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT
FALSE | FALSE | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT
FALSE | FALSE | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT
FALSE | FALSE | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT
FALSE | FALSE | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT
FALSE | FALSE | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT
FALSE | FALSE | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT
FALSE | FALSE | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT
FALSE | FALSE | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT
FALSE | FALSE | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT
FALSE | FALSE | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT
FALSE | FALSE | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT
FALSE | FALSE | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT
FALSE | FALSE | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT
FALSE | FALSE | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT
FALSE | FALSE | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT
FALSE | FALSE | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT
FALSE | FALSE | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT
FALSE | FALSE | 7167 | 00000149 | Im BT Total kVArh | 7166 | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT
FALSE | FALSE | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT
FALSE | FALSE | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT
Im_total_kWh | 86 | 7173 | 00000269 | Im Total kWh | 7172 | 7172 | Used | Im_total_kWh | 86 | float | AI | 0.001 | 0 | Im_total_kWh | 7172 | 3 | FLOAT
FALSE | FALSE | 7175 | 00001129 | Ex PV KVarh | 7174 | 7180 |  | Ex_Total_kVAr | 87 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
#N/A | #N/A | 7177 | 00008129 | Ex PV KVarh Time | 7176 | 7174 |  | Ex PV KVarh | 88 | float | AI | 0.001 | 0 | Ex PV KVarh | 7174 | 3 | FLOAT
FALSE | FALSE | 7181 | 00001149 | Ex Total kVAr | 7180 | 7182 |  | No_of_Reset | 89 | float | AI | 1 | 0 | No_of_Reset | 7182 | 3 | SHORT
FALSE | FALSE | 7183 | 0000F032 | NB Reset | 7182
#N/A | #N/A | 7185 | 00008020 | Ex PV kW A Time | 7184
#N/A | #N/A | 7189 | 00008021 | Ex PV kW B Time | 7188
#N/A | #N/A | 7193 | 00008022 | Ex PV kW C Time | 7192

## INI
Check |  | METER |  |  |  | Enos
Inst_kW | 0 | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | -0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Inst_kVAr | 1 | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | -0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Im_Total_kWh | 2 | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Im_Total_kWh | 2 | float | AI | 0.001 | 0 | Im_Total_kWh | 7004 | 3 | FLOAT
Im_kWh_RateA | 3 | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Im_kWh_RateA | 3 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7006 | 3 | FLOAT
Im_kWh_RateB | 4 | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Im_kWh_RateB | 4 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7008 | 3 | FLOAT
Im_kWh_RateC | 5 | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Im_kWh_RateC | 5 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7010 | 3 | FLOAT
FALSE | FALSE | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Im_Max_kW_A | 6 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7012 | 3 | FLOAT
FALSE | FALSE | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Im_Max_kW_B | 7 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7014 | 3 | FLOAT
FALSE | FALSE | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Im_Max_kW_C | 8 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7016 | 3 | FLOAT
FALSE | FALSE | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Im_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7018 | 3 | FLOAT
FALSE | FALSE | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Im_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7020 | 3 | FLOAT
FALSE | FALSE | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Im_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7022 | 3 | FLOAT
Im_Total_kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Im_Total_kVArh | 12 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7024 | 3 | FLOAT
FALSE | FALSE | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Im_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7026 | 3 | FLOAT
FALSE | FALSE | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Im_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7028 | 3 | FLOAT
FALSE | FALSE | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Im_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7030 | 3 | FLOAT
FALSE | FALSE | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Im_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7032 | 3 | FLOAT
FALSE | FALSE | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Im_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7034 | 3 | FLOAT
FALSE | FALSE | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Im_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7036 | 3 | FLOAT
FALSE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Im_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7038 | 3 | FLOAT
FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Im_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7040 | 3 | FLOAT
FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Im_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7042 | 3 | FLOAT
FALSE | FALSE | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 |  | Im_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7044 | 3 | FLOAT
FALSE | FALSE | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 |  | Im_BT_kWhA | 23 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7046 | 3 | FLOAT
FALSE | FALSE | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 |  | Im_BT_kWhB | 24 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7048 | 3 | FLOAT
FALSE | FALSE | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 |  | Im_BT_kWhC | 25 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7050 | 3 | FLOAT
FALSE | FALSE | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Im_PV_kW_A | 26 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7052 | 3 | FLOAT
FALSE | FALSE | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Im_PV_kW_B | 27 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7054 | 3 | FLOAT
FALSE | FALSE | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Im_PV_kW_C | 28 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7056 | 3 | FLOAT
FALSE | FALSE | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 |  | Im_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Im_kW_Cum_A2 | 7058 | 3 | FLOAT
FALSE | FALSE | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 |  | Im_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Im_kW_Cum_B2 | 7060 | 3 | FLOAT
FALSE | FALSE | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 |  | Im_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Im_kW_Cum_C2 | 7062 | 3 | FLOAT
FALSE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | 7064 | 7064 |  | Im_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7064 | 3 | FLOAT
FALSE | FALSE | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Im_PV_kVAr | 33 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7066 | 3 | FLOAT
FALSE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Im_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7068 | 3 | FLOAT
FALSE | FALSE | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
FALSE | FALSE | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
FALSE | FALSE | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
FALSE | FALSE | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
FALSE | FALSE | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
FALSE | FALSE | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
FALSE | FALSE | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
FALSE | FALSE | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
FALSE | FALSE | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
FALSE | FALSE | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
FALSE | FALSE | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
FALSE | FALSE | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
FALSE | FALSE | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
FALSE | FALSE | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
FALSE | FALSE | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
FALSE | FALSE | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
FALSE | FALSE | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
FALSE | FALSE | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
FALSE | FALSE | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
FALSE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
FALSE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
FALSE | FALSE | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Ex_kWh_RateA | 57 | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Ex_kWh_RateA | 57 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7114 | 3 | FLOAT
Ex_kWh_RateB | 58 | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Ex_kWh_RateB | 58 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7116 | 3 | FLOAT
Ex_kWh_RateC | 59 | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Ex_kWh_RateC | 59 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7118 | 3 | FLOAT
FALSE | FALSE | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Ex_Max_kW_A | 60 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7120 | 3 | FLOAT
FALSE | FALSE | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Ex_Max_kW_B | 61 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7122 | 3 | FLOAT
FALSE | FALSE | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Ex_Max_kW_C | 62 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7124 | 3 | FLOAT
Ex_Total_kVArh | 63 | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Ex_Total_kVArh | 63 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7126 | 3 | FLOAT
FALSE | FALSE | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Ex_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7128 | 3 | FLOAT
FALSE | FALSE | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Ex_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7130 | 3 | FLOAT
FALSE | FALSE | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Ex_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7132 | 3 | FLOAT
FALSE | FALSE | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Ex_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7134 | 3 | FLOAT
FALSE | FALSE | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Ex_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7136 | 3 | FLOAT
FALSE | FALSE | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Ex_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7138 | 3 | FLOAT
FALSE | FALSE | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Ex_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7140 | 3 | FLOAT
FALSE | FALSE | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Ex_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7142 | 3 | FLOAT
FALSE | FALSE | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Ex_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7144 | 3 | FLOAT
Ex_BT_Total_kWh | 73 | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 | Used | Ex_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7146 | 3 | FLOAT
Ex_BT_kWhA | 74 | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 | Used | Ex_BT_kWhA | 74 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7148 | 3 | FLOAT
Ex_BT_kWhB | 75 | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 | Used | Ex_BT_kWhB | 75 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7150 | 3 | FLOAT
Ex_BT_kWhC | 76 | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 | Used | Ex_BT_kWhC | 76 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7152 | 3 | FLOAT
FALSE | FALSE | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Ex_PV_kW_A | 77 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7154 | 3 | FLOAT
FALSE | FALSE | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Ex_PV_kW_B | 78 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7156 | 3 | FLOAT
FALSE | FALSE | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Ex_PV_kW_C | 79 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7158 | 3 | FLOAT
FALSE | FALSE | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Ex_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7160 | 3 | FLOAT
FALSE | FALSE | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Ex_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7162 | 3 | FLOAT
FALSE | FALSE | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Ex_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7164 | 3 | FLOAT
FALSE | FALSE | 7167 | 00000149 | Im BT Total kVArh | 7166 | 7166 |  | Ex_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7166 | 3 | FLOAT
FALSE | FALSE | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Ex_PV_kVAr | 84 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7168 | 3 | FLOAT
FALSE | FALSE | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Ex_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7170 | 3 | FLOAT
Ex_total_kWh | 86 | 7173 | 00000269 | Im Total kWh | 7172 | 7172 | Used | Ex_total_kWh | 86 | float | AI | 0.001 | 0 | Ex_total_kWh | 7172 | 3 | FLOAT
#N/A | #N/A | 7175 | 00001129 | Ex PV KVarh | 7174 | 7180 |  | Ex_Total_kVAr | 87 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
#N/A | #N/A | 7177 | 00008129 | Ex PV KVarh Time | 7176 | 7256 | Used | I_Total_KWh_2 | 88 | float | AI | 0.001 | 0 | Im_Total_KWh_2 | 7256 | 3 | FLOAT
FALSE | FALSE | 7181 | 00001149 | Ex Total kVAr | 7180 | 7250 | Used | I_total_KWh_RateA_2 | 89 | float | AI | 0.001 | 0 | Im_total_KWh_RateA_2 | 7250 | 3 | FLOAT
#N/A | #N/A | 7183 | 0000F032 | NB Reset | 7182 | 7252 | Used | I_total_KWh_RateB_2 | 90 | float | AI | 0.001 | 0 | Im_total_KWh_RateB_2 | 7252 | 3 | FLOAT
#N/A | #N/A | 7185 | 00008020 | Ex PV kW A Time | 7184 | 7254 | Used | I_total_KWh_RateC_2 | 91 | float | AI | 0.001 | 0 | Im_total_KWh_RateC_2 | 7254 | 3 | FLOAT
#N/A | #N/A | 7189 | 00008021 | Ex PV kW B Time | 7188
#N/A | #N/A | 7193 | 00008022 | Ex PV kW C Time | 7192
| #N/A | 7300 | 0000F03D | Date_time
| #N/A | 7400 | 0000FC00 | date_to_reset_meter
| #N/A | 7207 | 0000F092 | check_lcd
| #N/A | 7209 | 0000F032 | count_reset
| #N/A | 7251 | 00000260 | Im total KWh Rate A
| #N/A | 7253 | 00000261 | Im total KWh Rate B
| #N/A | 7255 | 00000262 | Im total KWh Rate C
| #N/A | 7257 | 00000269 | Im total KWh 2

## Check
|  | Inverter | Check | Revenue Meter | Check | Pyranometer | Check
VISTEC1 | VT1 | 6 | TRUE | 6 | FALSE | 0 | FALSE
VISTEC2 | VT2 | 11 | TRUE | 3 | FALSE | 1 | FALSE
KVIS | KVIS | 1 | TRUE | 1 | FALSE | 0 | FALSE
Thaioil1 | TO1 | 7 | TRUE | 1 | FALSE | 1 | TRUE
Thaioil2 | TO2 | 5 | TRUE | 4 | FALSE | 1 | FALSE
PTTOR MINBURI | PTTMB | 2 | TRUE | 2 | FALSE | 0 | FALSE
PTTOR TALINCHAN | PTTTL | 1 | TRUE | 1 | FALSE | 0 | FALSE
AICA | AICA | 30 | TRUE | 2 | FALSE | 1 | FALSE
SURETEX | SRT | 17 | TRUE | 2 | FALSE | 1 | FALSE
SUT | SUT | 31 | TRUE | 6 | FALSE | 2 | FALSE
PTIC | PTIC | 2 | TRUE | 1 | FALSE | 1 | TRUE
RASC | RASC | 3 | TRUE | 1 | FALSE | 1 | TRUE
ENTER | ENT | 9 | TRUE | 2 | FALSE | 1 | FALSE
INI | INI | 14 | TRUE | 2 | FALSE | 5 | FALSE | 2
FUTUREFLEX | FTF | 7 | TRUE | 2 | FALSE | 2 | TRUE

## Compare Meter
VT1&VT2&KVIS |  |  |  | TOP1 |  |  |  |  | TOP2 |  |  |  |  | Minburi |  |  |  |  | AICA |  |  |  |  | SURETEX |  |  |  |  | SUT |  |  |  |  | PTIC |  |  |  |  | INI |  |  |  |  | RASC |  |  |  |  | ENTER |  |  |  |  | Futureflex
7001 | 0000E033 | Inst kW | 0 | 7001 | 0000E033 | Inst kW | TRUE | 0 | 7001 | 0000E033 | Inst kW | TRUE | 0 | 7001 | 00000069 | Ex Total kWh | FALSE | 9 | 7001 | 0000E033 | Inst kW | TRUE | 0 | 7001 | 0000E033 | Inst kW | TRUE | 0 | 7001 | 0000E033 | Inst kW | TRUE | 0 | 7001 | 0000E033 | Inst kW | TRUE | 0 | 7001 | 0000E033 | Inst kW | TRUE | 0 | 7001 | 0000E033 | Inst kW | TRUE | 0 | 7001 | 0000E033 | Inst kW | TRUE | 0 | 7001 | 0000E033 | Inst kW | TRUE | 0
7003 | 0000E043 | Inst kVAr | 1 | 7003 | 0000E043 | Inst kVAr | TRUE | 1 | 7003 | 0000E043 | Inst kVAr | TRUE | 1 | 7003 | 00000060 | Ex kWh RateA | FALSE | 19 | 7003 | 0000E043 | Inst kVAr | TRUE | 1 | 7003 | 0000E043 | Inst kVAr | TRUE | 1 | 7003 | 0000E043 | Inst kVAr | TRUE | 1 | 7003 | 0000E043 | Inst kVAr | TRUE | 1 | 7003 | 0000E043 | Inst kVAr | TRUE | 1 | 7003 | 0000E043 | Inst kVAr | TRUE | 1 | 7003 | 0000E043 | Inst kVAr | TRUE | 1 | 7003 | 0000E043 | Inst kVAr | TRUE | 1
7005 | 00000069 | Ex Total kWh | 2 | 7005 | 00000069 | Ex Total kWh | TRUE | 2 | 7005 | 00000069 | Ex Total kWh | TRUE | 2 | 7005 | 00000061 | Ex kWh RateB | FALSE | 20 | 7005 | 00000069 | Ex Total kWh | TRUE | 2 | 7005 | 00000069 | Ex Total kWh | TRUE | 2 | 7005 | 00000069 | Ex Total kWh | TRUE | 2 | 7005 | 00000069 | Ex Total kWh | TRUE | 2 | 7005 | 00000069 | Ex Total kWh | TRUE | 2 | 7005 | 00000069 | Ex Total kWh | TRUE | 2 | 7005 | 00000069 | Ex Total kWh | TRUE | 2 | 7005 | 00000069 | Ex Total kWh | TRUE | 2
7007 | 00000000 | Ex kWh RateA | 3 | 7007 | 00000000 | Ex kWh RateA | TRUE | 3 | 7007 | 00000000 | Ex kWh RateA | TRUE | 3 | 7007 | 00000062 | Ex kWh RateC | FALSE | 21 | 7007 | 00000000 | Ex kWh RateA | TRUE | 3 | 7007 | 00000000 | Ex kWh RateA | TRUE | 3 | 7007 | 00000000 | Ex kWh RateA | TRUE | 3 | 7007 | 00000000 | Ex kWh RateA | TRUE | 3 | 7007 | 00000000 | Ex kWh RateA | TRUE | 3 | 7007 | 00000000 | Ex kWh RateA | TRUE | 3 | 7007 | 00000000 | Ex kWh RateA | TRUE | 3 | 7007 | 00000000 | Ex kWh RateA | TRUE | 3
7009 | 00000001 | Ex kWh RateB | 4 | 7009 | 00000001 | Ex kWh RateB | TRUE | 4 | 7009 | 00000001 | Ex kWh RateB | TRUE | 4 | 7009 | 00001000 | Ex Max kW A | FALSE | 15 | 7009 | 00000001 | Ex kWh RateB | TRUE | 4 | 7009 | 00000001 | Ex kWh RateB | TRUE | 4 | 7009 | 00000001 | Ex kWh RateB | TRUE | 4 | 7009 | 00000001 | Ex kWh RateB | TRUE | 4 | 7009 | 00000001 | Ex kWh RateB | TRUE | 4 | 7009 | 00000001 | Ex kWh RateB | TRUE | 4 | 7009 | 00000001 | Ex kWh RateB | TRUE | 4 | 7009 | 00000001 | Ex kWh RateB | TRUE | 4
7011 | 00000002 | Ex kWh RateC | 5 | 7011 | 00000002 | Ex kWh RateC | TRUE | 5 | 7011 | 00000002 | Ex kWh RateC | TRUE | 5 | 7011 | 00001001 | Ex Max kW B | FALSE | 16 | 7011 | 00000002 | Ex kWh RateC | TRUE | 5 | 7011 | 00000002 | Ex kWh RateC | TRUE | 5 | 7011 | 00000002 | Ex kWh RateC | TRUE | 5 | 7011 | 00000002 | Ex kWh RateC | TRUE | 5 | 7011 | 00000002 | Ex kWh RateC | TRUE | 5 | 7011 | 00000002 | Ex kWh RateC | TRUE | 5 | 7011 | 00000002 | Ex kWh RateC | TRUE | 5 | 7011 | 00000002 | Ex kWh RateC | TRUE | 5
7013 | 00001000 | Ex Max kW A | FALSE | 7013 | 00001000 | Ex Max kW A | TRUE | FALSE | 7013 | 00001000 | Ex Max kW A | TRUE | FALSE | 7013 | 00001002 | Ex Max kW C | FALSE | 17 | 7013 | 00001000 | Ex Max kW A | TRUE | FALSE | 7013 | 00001000 | Ex Max kW A | TRUE | FALSE | 7013 | 00001000 | Ex Max kW A | TRUE | FALSE | 7013 | 00001000 | Ex Max kW A | TRUE | FALSE | 7013 | 00001000 | Ex Max kW A | TRUE | FALSE | 7013 | 00001000 | Ex Max kW A | TRUE | FALSE | 7013 | 00001000 | Ex Max kW A | TRUE | FALSE | 7013 | 00001000 | Ex Max kW A | TRUE | FALSE
7015 | 00001001 | Ex Max kW B | FALSE | 7015 | 00001001 | Ex Max kW B | TRUE | FALSE | 7015 | 00001001 | Ex Max kW B | TRUE | FALSE | 7015 | 00001040 | Ex kW-Cum A | FALSE | #N/A | 7015 | 00001001 | Ex Max kW B | TRUE | FALSE | 7015 | 00001001 | Ex Max kW B | TRUE | FALSE | 7015 | 00001001 | Ex Max kW B | TRUE | FALSE | 7015 | 00001001 | Ex Max kW B | TRUE | FALSE | 7015 | 00001001 | Ex Max kW B | TRUE | FALSE | 7015 | 00001001 | Ex Max kW B | TRUE | FALSE | 7015 | 00001001 | Ex Max kW B | TRUE | FALSE | 7015 | 00001001 | Ex Max kW B | TRUE | FALSE
7017 | 00001002 | Ex Max kW C | FALSE | 7017 | 00001002 | Ex Max kW C | TRUE | FALSE | 7017 | 00001002 | Ex Max kW C | TRUE | FALSE | 7017 | 00001041 | Ex kW-Cum B | FALSE | #N/A | 7017 | 00001002 | Ex Max kW C | TRUE | FALSE | 7017 | 00001002 | Ex Max kW C | TRUE | FALSE | 7017 | 00001002 | Ex Max kW C | TRUE | FALSE | 7017 | 00001002 | Ex Max kW C | TRUE | FALSE | 7017 | 00001002 | Ex Max kW C | TRUE | FALSE | 7017 | 00001002 | Ex Max kW C | TRUE | FALSE | 7017 | 00001002 | Ex Max kW C | TRUE | FALSE | 7017 | 00001002 | Ex Max kW C | TRUE | FALSE
7019 | 00001040 | Ex kW-Cum A | FALSE | 7019 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7019 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7019 | 00001042 | Ex kW-Cum C | FALSE | #N/A | 7019 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7019 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7019 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7019 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7019 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7019 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7019 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7019 | 00001040 | Ex kW-Cum A | TRUE | FALSE
7021 | 00001041 | Ex kW-Cum B | FALSE | 7021 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7021 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7021 | 00000169 | Ex Total kVArh | FALSE | 10 | 7021 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7021 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7021 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7021 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7021 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7021 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7021 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7021 | 00001041 | Ex kW-Cum B | TRUE | FALSE
7023 | 00001042 | Ex kW-Cum C | FALSE | 7023 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7023 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7023 | 00000160 | Ex kVArh A | FALSE | #N/A | 7023 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7023 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7023 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7023 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7023 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7023 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7023 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7023 | 00001042 | Ex kW-Cum C | TRUE | FALSE
7025 | 00000169 | Ex Total kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | TRUE | 12 | 7025 | 00000169 | Ex Total kVArh | TRUE | 12 | 7025 | 00000161 | Ex kVArh B | FALSE | #N/A | 7025 | 00000169 | Ex Total kVArh | TRUE | 12 | 7025 | 00000169 | Ex Total kVArh | TRUE | 12 | 7025 | 00000169 | Ex Total kVArh | TRUE | 12 | 7025 | 00000169 | Ex Total kVArh | TRUE | 12 | 7025 | 00000169 | Ex Total kVArh | TRUE | 12 | 7025 | 00000169 | Ex Total kVArh | TRUE | 12 | 7025 | 00000169 | Ex Total kVArh | TRUE | 12 | 7025 | 00000169 | Ex Total kVArh | TRUE | 12
7027 | 00000160 | Ex kVArh A | FALSE | 7027 | 00000160 | Ex kVArh A | TRUE | FALSE | 7027 | 00000160 | Ex kVArh A | TRUE | FALSE | 7027 | 00000162 | Ex kVArh C | FALSE | #N/A | 7027 | 00000160 | Ex kVArh A | TRUE | FALSE | 7027 | 00000160 | Ex kVArh A | TRUE | FALSE | 7027 | 00000160 | Ex kVArh A | TRUE | FALSE | 7027 | 00000160 | Ex kVArh A | TRUE | FALSE | 7027 | 00000160 | Ex kVArh A | TRUE | FALSE | 7027 | 00000160 | Ex kVArh A | TRUE | FALSE | 7027 | 00000160 | Ex kVArh A | TRUE | FALSE | 7027 | 00000160 | Ex kVArh A | TRUE | FALSE
7029 | 00000161 | Ex kVArh B | FALSE | 7029 | 00000161 | Ex kVArh B | TRUE | FALSE | 7029 | 00000161 | Ex kVArh B | TRUE | FALSE | 7029 | 00001100 | Ex Max kVAr A | FALSE | #N/A | 7029 | 00000161 | Ex kVArh B | TRUE | FALSE | 7029 | 00000161 | Ex kVArh B | TRUE | FALSE | 7029 | 00000161 | Ex kVArh B | TRUE | FALSE | 7029 | 00000161 | Ex kVArh B | TRUE | FALSE | 7029 | 00000161 | Ex kVArh B | TRUE | FALSE | 7029 | 00000161 | Ex kVArh B | TRUE | FALSE | 7029 | 00000161 | Ex kVArh B | TRUE | FALSE | 7029 | 00000161 | Ex kVArh B | TRUE | FALSE
7031 | 00000162 | Ex kVArh C | FALSE | 7031 | 00000162 | Ex kVArh C | TRUE | FALSE | 7031 | 00000162 | Ex kVArh C | TRUE | FALSE | 7031 | 00001101 | Ex Max kVAr B | FALSE | #N/A | 7031 | 00000162 | Ex kVArh C | TRUE | FALSE | 7031 | 00000162 | Ex kVArh C | TRUE | FALSE | 7031 | 00000162 | Ex kVArh C | TRUE | FALSE | 7031 | 00000162 | Ex kVArh C | TRUE | FALSE | 7031 | 00000162 | Ex kVArh C | TRUE | FALSE | 7031 | 00000162 | Ex kVArh C | TRUE | FALSE | 7031 | 00000162 | Ex kVArh C | TRUE | FALSE | 7031 | 00000162 | Ex kVArh C | TRUE | FALSE
7033 | 00001100 | Ex Max kVArh A | FALSE | 7033 | 00001100 | Ex Max kVArh A | TRUE | FALSE | 7033 | 00001100 | Ex Max kVArh A | TRUE | FALSE | 7033 | 00001102 | Ex Max kVAr C | FALSE | #N/A | 7033 | 00001100 | Ex Max kVArh A | TRUE | FALSE | 7033 | 00001100 | Ex Max kVArh A | TRUE | FALSE | 7033 | 00001100 | Ex Max kVArh A | TRUE | FALSE | 7033 | 00001100 | Ex Max kVArh A | TRUE | FALSE | 7033 | 00001100 | Ex Max kVArh A | TRUE | FALSE | 7033 | 00001100 | Ex Max kVArh A | TRUE | FALSE | 7033 | 00001100 | Ex Max kVArh A | TRUE | FALSE | 7033 | 00001100 | Ex Max kVArh A | TRUE | FALSE
7035 | 00001101 | Ex Max kVArh B | FALSE | 7035 | 00001101 | Ex Max kVArh B | TRUE | FALSE | 7035 | 00001101 | Ex Max kVArh B | TRUE | FALSE | 7035 | 00000140 | Ex kVArh-Cum A | FALSE | #N/A | 7035 | 00001101 | Ex Max kVArh B | TRUE | FALSE | 7035 | 00001101 | Ex Max kVArh B | TRUE | FALSE | 7035 | 00001101 | Ex Max kVArh B | TRUE | FALSE | 7035 | 00001101 | Ex Max kVArh B | TRUE | FALSE | 7035 | 00001101 | Ex Max kVArh B | TRUE | FALSE | 7035 | 00001101 | Ex Max kVArh B | TRUE | FALSE | 7035 | 00001101 | Ex Max kVArh B | TRUE | FALSE | 7035 | 00001101 | Ex Max kVArh B | TRUE | FALSE
7037 | 00001102 | Ex Max kVArh C | FALSE | 7037 | 00001102 | Ex Max kVArh C | TRUE | FALSE | 7037 | 00001102 | Ex Max kVArh C | TRUE | FALSE | 7037 | 00000141 | Ex kVArh-Cum B | FALSE | #N/A | 7037 | 00001102 | Ex Max kVArh C | TRUE | FALSE | 7037 | 00001102 | Ex Max kVArh C | TRUE | FALSE | 7037 | 00001102 | Ex Max kVArh C | TRUE | FALSE | 7037 | 00001102 | Ex Max kVArh C | TRUE | FALSE | 7037 | 00001102 | Ex Max kVArh C | TRUE | FALSE | 7037 | 00001102 | Ex Max kVArh C | TRUE | FALSE | 7037 | 00001102 | Ex Max kVArh C | TRUE | FALSE | 7037 | 00001102 | Ex Max kVArh C | TRUE | FALSE
7039 | 00000140 | Ex kVArh-Cum A | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | TRUE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | TRUE | FALSE | 7039 | 00000142 | Ex kVArh-Cum C | FALSE | #N/A | 7039 | 00000140 | Ex kVArh-Cum A | TRUE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | TRUE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | TRUE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | TRUE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | TRUE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | TRUE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | TRUE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | TRUE | FALSE
7041 | 00000141 | Ex kVArh-Cum B | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | TRUE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | TRUE | FALSE | 7041 | 0000E000 | Ph A Volt | FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | TRUE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | TRUE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | TRUE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | TRUE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | TRUE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | TRUE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | TRUE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | TRUE | FALSE
7043 | 00000142 | Ex kVArh-Cum C | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | TRUE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | TRUE | FALSE | 7043 | 0000E001 | Ph B Volt | FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | TRUE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | TRUE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | TRUE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | TRUE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | TRUE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | TRUE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | TRUE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | TRUE | FALSE
7045 | 00000049 | Ex BT Total kWh | 22 | 7045 | 00000049 | Ex BT Total kWh | TRUE | FALSE | 7045 | 00000049 | Ex BT Total kWh | TRUE | FALSE | 7045 | 0000E002 | Ph C Volt | FALSE | FALSE | 7045 | 00000049 | Ex BT Total kWh | TRUE | 22 | 7045 | 00000049 | Ex BT Total kWh | TRUE | 22 | 7045 | 00000049 | Ex BT Total kWh | TRUE | 22 | 7045 | 00000049 | Ex BT Total kWh | TRUE | 22 | 7045 | 00000049 | Ex BT Total kWh | TRUE | FALSE | 7045 | 00000049 | Ex BT Total kWh | TRUE | 22 | 7045 | 00000049 | Ex BT Total kWh | TRUE | 22 | 7045 | 00000049 | Ex BT Total kWh | TRUE | FALSE
7047 | 00000040 | Ex BT kWhA | 23 | 7047 | 00000040 | Ex BT kWhA | TRUE | FALSE | 7047 | 00000040 | Ex BT kWhA | TRUE | FALSE | 7047 | 0000E010 | Ph A Curr | FALSE | 4 | 7047 | 00000040 | Ex BT kWhA | TRUE | 23 | 7047 | 00000040 | Ex BT kWhA | TRUE | 23 | 7047 | 00000040 | Ex BT kWhA | TRUE | 23 | 7047 | 00000040 | Ex BT kWhA | TRUE | 23 | 7047 | 00000040 | Ex BT kWhA | TRUE | FALSE | 7047 | 00000040 | Ex BT kWhA | TRUE | 23 | 7047 | 00000040 | Ex BT kWhA | TRUE | 23 | 7047 | 00000040 | Ex BT kWhA | TRUE | FALSE
7049 | 00000041 | Ex BT kWhB | 24 | 7049 | 00000041 | Ex BT kWhB | TRUE | FALSE | 7049 | 00000041 | Ex BT kWhB | TRUE | FALSE | 7049 | 0000E011 | Ph B Curr | FALSE | 5 | 7049 | 00000041 | Ex BT kWhB | TRUE | 24 | 7049 | 00000041 | Ex BT kWhB | TRUE | 24 | 7049 | 00000041 | Ex BT kWhB | TRUE | 24 | 7049 | 00000041 | Ex BT kWhB | TRUE | 24 | 7049 | 00000041 | Ex BT kWhB | TRUE | FALSE | 7049 | 00000041 | Ex BT kWhB | TRUE | 24 | 7049 | 00000041 | Ex BT kWhB | TRUE | 24 | 7049 | 00000041 | Ex BT kWhB | TRUE | FALSE
7051 | 00000042 | Ex BT kWhC | 25 | 7051 | 00000042 | Ex BT kWhC | TRUE | FALSE | 7051 | 00000042 | Ex BT kWhC | TRUE | FALSE | 7051 | 0000E012 | Ph C Curr | FALSE | 6 | 7051 | 00000042 | Ex BT kWhC | TRUE | 25 | 7051 | 00000042 | Ex BT kWhC | TRUE | 25 | 7051 | 00000042 | Ex BT kWhC | TRUE | 25 | 7051 | 00000042 | Ex BT kWhC | TRUE | 25 | 7051 | 00000042 | Ex BT kWhC | TRUE | FALSE | 7051 | 00000042 | Ex BT kWhC | TRUE | 25 | 7051 | 00000042 | Ex BT kWhC | TRUE | 25 | 7051 | 00000042 | Ex BT kWhC | TRUE | FALSE
7053 | 00001020 | Ex PV kW A | FALSE | 7053 | 00001020 | Ex PV kW A | TRUE | FALSE | 7053 | 00001020 | Ex PV kW A | TRUE | FALSE | 7053 | 0000E020 | Ph A angle | FALSE | #N/A | 7053 | 00001020 | Ex PV kW A | TRUE | FALSE | 7053 | 00001020 | Ex PV kW A | TRUE | FALSE | 7053 | 00001020 | Ex PV kW A | TRUE | FALSE | 7053 | 00001020 | Ex PV kW A | TRUE | FALSE | 7053 | 00001020 | Ex PV kW A | TRUE | FALSE | 7053 | 00001020 | Ex PV kW A | TRUE | FALSE | 7053 | 00001020 | Ex PV kW A | TRUE | FALSE | 7053 | 00001020 | Ex PV kW A | TRUE | FALSE
7055 | 00001021 | Ex PV kW B | FALSE | 7055 | 00001021 | Ex PV kW B | TRUE | FALSE | 7055 | 00001021 | Ex PV kW B | TRUE | FALSE | 7055 | 0000E021 | Ph B angle | FALSE | #N/A | 7055 | 00001021 | Ex PV kW B | TRUE | FALSE | 7055 | 00001021 | Ex PV kW B | TRUE | FALSE | 7055 | 00001021 | Ex PV kW B | TRUE | FALSE | 7055 | 00001021 | Ex PV kW B | TRUE | FALSE | 7055 | 00001021 | Ex PV kW B | TRUE | FALSE | 7055 | 00001021 | Ex PV kW B | TRUE | FALSE | 7055 | 00001021 | Ex PV kW B | TRUE | FALSE | 7055 | 00001021 | Ex PV kW B | TRUE | FALSE
7057 | 00001022 | Ex PV kW C | FALSE | 7057 | 00001022 | Ex PV kW C | TRUE | FALSE | 7057 | 00001022 | Ex PV kW C | TRUE | FALSE | 7057 | 0000E022 | Ph C angle | FALSE | #N/A | 7057 | 00001022 | Ex PV kW C | TRUE | FALSE | 7057 | 00001022 | Ex PV kW C | TRUE | FALSE | 7057 | 00001022 | Ex PV kW C | TRUE | FALSE | 7057 | 00001022 | Ex PV kW C | TRUE | FALSE | 7057 | 00001022 | Ex PV kW C | TRUE | FALSE | 7057 | 00001022 | Ex PV kW C | TRUE | FALSE | 7057 | 00001022 | Ex PV kW C | TRUE | FALSE | 7057 | 00001022 | Ex PV kW C | TRUE | FALSE
7059 | 00001040 | Ex kW-Cum A | 29 | 7059 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7059 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7059 | 0000E060 | Frequency | FALSE | FALSE | 7059 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7059 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7059 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7059 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7059 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7059 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7059 | 00001040 | Ex kW-Cum A | TRUE | FALSE | 7059 | 00001040 | Ex kW-Cum A | TRUE | FALSE
7061 | 00001041 | Ex kW-Cum B | 30 | 7061 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7061 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7061 | 0000E026 | Power Factor | FALSE | 8 | 7061 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7061 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7061 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7061 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7061 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7061 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7061 | 00001041 | Ex kW-Cum B | TRUE | FALSE | 7061 | 00001041 | Ex kW-Cum B | TRUE | FALSE
7063 | 00001042 | Ex kW-Cum C | 31 | 7063 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7063 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7063 | 0000F03D | Current DateTime | FALSE | #N/A | 7063 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7063 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7063 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7063 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7063 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7063 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7063 | 00001042 | Ex kW-Cum C | TRUE | FALSE | 7063 | 00001042 | Ex kW-Cum C | TRUE | FALSE
7065 | 00000149 | Ex BT Total kVAr | 32 | 7065 | 00000149 | Ex BT Total kVAr | TRUE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | TRUE | FALSE | 7069 | 0000FC00 | DT LastReset | FALSE | #N/A | 7065 | 00000149 | Ex BT Total kVAr | TRUE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | TRUE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | TRUE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | TRUE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | TRUE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | TRUE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | TRUE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | TRUE | FALSE
7067 | 00000129 | Ex PV kVAr | FALSE | 7067 | 00000129 | Ex PV kVAr | TRUE | FALSE | 7067 | 00000129 | Ex PV kVAr | TRUE | FALSE | 7075 | 0000F032 | No.of reset | FALSE | #N/A | 7067 | 00000129 | Ex PV kVAr | TRUE | FALSE | 7067 | 00000129 | Ex PV kVAr | TRUE | FALSE | 7067 | 00000129 | Ex PV kVAr | TRUE | FALSE | 7067 | 00000129 | Ex PV kVAr | TRUE | FALSE | 7067 | 00000129 | Ex PV kVAr | TRUE | FALSE | 7067 | 00000129 | Ex PV kVAr | TRUE | FALSE | 7067 | 00000129 | Ex PV kVAr | TRUE | FALSE | 7067 | 00000129 | Ex PV kVAr | TRUE | FALSE
7069 | 00000169 | Ex kVAr-Cum | FALSE | 7069 | 00000169 | Ex kVAr-Cum | TRUE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | TRUE | FALSE | 7077 | 0000F540 | CT ratio | FALSE | #N/A | 7069 | 00000169 | Ex kVAr-Cum | TRUE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | TRUE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | TRUE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | TRUE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | TRUE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | TRUE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | TRUE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | TRUE | FALSE
7071 | 0000E000 | Ph A Volt | FALSE | 7071 | 0000E000 | Ph A Volt | TRUE | FALSE | 7071 | 0000E000 | Ph A Volt | TRUE | FALSE | 7079 | 0000F541 | VT ratio | FALSE | #N/A | 7071 | 0000E000 | Ph A Volt | TRUE | 35 | 7071 | 0000E000 | Ph A Volt | TRUE | FALSE | 7071 | 0000E000 | Ph A Volt | TRUE | FALSE | 7071 | 0000E000 | Ph A Volt | TRUE | FALSE | 7071 | 0000E000 | Ph A Volt | TRUE | FALSE | 7071 | 0000E000 | Ph A Volt | TRUE | FALSE | 7071 | 0000E000 | Ph A Volt | TRUE | FALSE | 7071 | 0000E000 | Ph A Volt | TRUE | FALSE
7073 | 0000E001 | Ph B Volt | FALSE | 7073 | 0000E001 | Ph B Volt | TRUE | FALSE | 7073 | 0000E001 | Ph B Volt | TRUE | FALSE | 7081 | 0000FC20 | Last PowerDown | FALSE | #N/A | 7073 | 0000E001 | Ph B Volt | TRUE | 36 | 7073 | 0000E001 | Ph B Volt | TRUE | FALSE | 7073 | 0000E001 | Ph B Volt | TRUE | FALSE | 7073 | 0000E001 | Ph B Volt | TRUE | FALSE | 7073 | 0000E001 | Ph B Volt | TRUE | FALSE | 7073 | 0000E001 | Ph B Volt | TRUE | FALSE | 7073 | 0000E001 | Ph B Volt | TRUE | FALSE | 7073 | 0000E001 | Ph B Volt | TRUE | FALSE
7075 | 0000E002 | Ph C Volt | FALSE | 7075 | 0000E002 | Ph C Volt | TRUE | FALSE | 7075 | 0000E002 | Ph C Volt | TRUE | FALSE | 7087 | 0000F093 | Last PowerUP | FALSE | #N/A | 7075 | 0000E002 | Ph C Volt | TRUE | 37 | 7075 | 0000E002 | Ph C Volt | TRUE | FALSE | 7075 | 0000E002 | Ph C Volt | TRUE | FALSE | 7075 | 0000E002 | Ph C Volt | TRUE | FALSE | 7075 | 0000E002 | Ph C Volt | TRUE | FALSE | 7075 | 0000E002 | Ph C Volt | TRUE | FALSE | 7075 | 0000E002 | Ph C Volt | TRUE | FALSE | 7075 | 0000E002 | Ph C Volt | TRUE | FALSE
7077 | 0000E010 | Ph A Curr | FALSE | 7077 | 0000E010 | Ph A Curr | TRUE | FALSE | 7077 | 0000E010 | Ph A Curr | TRUE | FALSE | 7093 | 0000F016 | Current Alarm | FALSE | #N/A | 7077 | 0000E010 | Ph A Curr | TRUE | 38 | 7077 | 0000E010 | Ph A Curr | TRUE | FALSE | 7077 | 0000E010 | Ph A Curr | TRUE | FALSE | 7077 | 0000E010 | Ph A Curr | TRUE | FALSE | 7077 | 0000E010 | Ph A Curr | TRUE | FALSE | 7077 | 0000E010 | Ph A Curr | TRUE | FALSE | 7077 | 0000E010 | Ph A Curr | TRUE | FALSE | 7077 | 0000E010 | Ph A Curr | TRUE | FALSE
7079 | 0000E011 | Ph B Curr | FALSE | 7079 | 0000E011 | Ph B Curr | TRUE | FALSE | 7079 | 0000E011 | Ph B Curr | TRUE | FALSE | 7101 | 0000F017 | Latched Alarm | FALSE | #N/A | 7079 | 0000E011 | Ph B Curr | TRUE | 39 | 7079 | 0000E011 | Ph B Curr | TRUE | FALSE | 7079 | 0000E011 | Ph B Curr | TRUE | FALSE | 7079 | 0000E011 | Ph B Curr | TRUE | FALSE | 7079 | 0000E011 | Ph B Curr | TRUE | FALSE | 7079 | 0000E011 | Ph B Curr | TRUE | FALSE | 7079 | 0000E011 | Ph B Curr | TRUE | FALSE | 7079 | 0000E011 | Ph B Curr | TRUE | FALSE
7081 | 0000E012 | Ph C Curr | FALSE | 7081 | 0000E012 | Ph C Curr | TRUE | FALSE | 7081 | 0000E012 | Ph C Curr | TRUE | FALSE | 7115 | 00000269 | Ex Total kWh | FALSE | 11 | 7081 | 0000E012 | Ph C Curr | TRUE | 40 | 7081 | 0000E012 | Ph C Curr | TRUE | FALSE | 7081 | 0000E012 | Ph C Curr | TRUE | FALSE | 7081 | 0000E012 | Ph C Curr | TRUE | FALSE | 7081 | 0000E012 | Ph C Curr | TRUE | FALSE | 7081 | 0000E012 | Ph C Curr | TRUE | FALSE | 7081 | 0000E012 | Ph C Curr | TRUE | FALSE | 7081 | 0000E012 | Ph C Curr | TRUE | FALSE
7083 | 0000E020 | Ph A angle | FALSE | 7083 | 0000E020 | Ph A angle | TRUE | FALSE | 7083 | 0000E020 | Ph A angle | TRUE | FALSE | 7117 | 00000369 | Ex Total kWh | FALSE | 12 | 7083 | 0000E020 | Ph A angle | TRUE | FALSE | 7083 | 0000E020 | Ph A angle | TRUE | FALSE | 7083 | 0000E020 | Ph A angle | TRUE | FALSE | 7083 | 0000E020 | Ph A angle | TRUE | FALSE | 7083 | 0000E020 | Ph A angle | TRUE | FALSE | 7083 | 0000E020 | Ph A angle | TRUE | FALSE | 7083 | 0000E020 | Ph A angle | TRUE | FALSE | 7083 | 0000E020 | Ph A angle | TRUE | FALSE
7085 | 0000E021 | Ph B angle | FALSE | 7085 | 0000E021 | Ph B angle | TRUE | FALSE | 7085 | 0000E021 | Ph B angle | TRUE | FALSE | 7119 | 0000E033 | Active power | FALSE | 13 | 7085 | 0000E021 | Ph B angle | TRUE | FALSE | 7085 | 0000E021 | Ph B angle | TRUE | FALSE | 7085 | 0000E021 | Ph B angle | TRUE | FALSE | 7085 | 0000E021 | Ph B angle | TRUE | FALSE | 7085 | 0000E021 | Ph B angle | TRUE | FALSE | 7085 | 0000E021 | Ph B angle | TRUE | FALSE | 7085 | 0000E021 | Ph B angle | TRUE | FALSE | 7085 | 0000E021 | Ph B angle | TRUE | FALSE
7087 | 0000E022 | Ph C angle | FALSE | 7087 | 0000E022 | Ph C angle | TRUE | FALSE | 7087 | 0000E022 | Ph C angle | TRUE | FALSE | 7121 | 0000E043 | Reactive power | FALSE | 14 | 7087 | 0000E022 | Ph C angle | TRUE | FALSE | 7087 | 0000E022 | Ph C angle | TRUE | FALSE | 7087 | 0000E022 | Ph C angle | TRUE | FALSE | 7087 | 0000E022 | Ph C angle | TRUE | FALSE | 7087 | 0000E022 | Ph C angle | TRUE | FALSE | 7087 | 0000E022 | Ph C angle | TRUE | FALSE | 7087 | 0000E022 | Ph C angle | TRUE | FALSE | 7087 | 0000E022 | Ph C angle | TRUE | FALSE
7089 | 0000E030 | Ph A Watts | FALSE | 7089 | 0000E030 | Ph A Watts | TRUE | FALSE | 7089 | 0000E030 | Ph A Watts | TRUE | FALSE | 7123 | 00000049 | Ex BT Total kWh | FALSE | #N/A | 7089 | 0000E030 | Ph A Watts | TRUE | FALSE | 7089 | 0000E030 | Ph A Watts | TRUE | FALSE | 7089 | 0000E030 | Ph A Watts | TRUE | FALSE | 7089 | 0000E030 | Ph A Watts | TRUE | FALSE | 7089 | 0000E030 | Ph A Watts | TRUE | FALSE | 7089 | 0000E030 | Ph A Watts | TRUE | FALSE | 7089 | 0000E030 | Ph A Watts | TRUE | FALSE | 7089 | 0000E030 | Ph A Watts | TRUE | FALSE
7091 | 0000E031 | Ph B Watts | FALSE | 7091 | 0000E031 | Ph B Watts | TRUE | FALSE | 7091 | 0000E031 | Ph B Watts | TRUE | FALSE | 7125 | 00000040 | Ex BT kWh Rate A | FALSE | #N/A | 7091 | 0000E031 | Ph B Watts | TRUE | FALSE | 7091 | 0000E031 | Ph B Watts | TRUE | FALSE | 7091 | 0000E031 | Ph B Watts | TRUE | FALSE | 7091 | 0000E031 | Ph B Watts | TRUE | FALSE | 7091 | 0000E031 | Ph B Watts | TRUE | FALSE | 7091 | 0000E031 | Ph B Watts | TRUE | FALSE | 7091 | 0000E031 | Ph B Watts | TRUE | FALSE | 7091 | 0000E031 | Ph B Watts | TRUE | FALSE
7093 | 0000E032 | Ph C Watts | FALSE | 7093 | 0000E032 | Ph C Watts | TRUE | FALSE | 7093 | 0000E032 | Ph C Watts | TRUE | FALSE | 7127 | 00000041 | Ex BT kWh Rate B | FALSE | #N/A | 7093 | 0000E032 | Ph C Watts | TRUE | FALSE | 7093 | 0000E032 | Ph C Watts | TRUE | FALSE | 7093 | 0000E032 | Ph C Watts | TRUE | FALSE | 7093 | 0000E032 | Ph C Watts | TRUE | FALSE | 7093 | 0000E032 | Ph C Watts | TRUE | FALSE | 7093 | 0000E032 | Ph C Watts | TRUE | FALSE | 7093 | 0000E032 | Ph C Watts | TRUE | FALSE | 7093 | 0000E032 | Ph C Watts | TRUE | FALSE
7095 | 0000E040 | Ph A vars | FALSE | 7095 | 0000E040 | Ph A vars | TRUE | FALSE | 7095 | 0000E040 | Ph A vars | TRUE | FALSE | 7129 | 00000042 | Ex BT kWh Rate C | FALSE | #N/A | 7095 | 0000E040 | Ph A vars | TRUE | FALSE | 7095 | 0000E040 | Ph A vars | TRUE | FALSE | 7095 | 0000E040 | Ph A vars | TRUE | FALSE | 7095 | 0000E040 | Ph A vars | TRUE | FALSE | 7095 | 0000E040 | Ph A vars | TRUE | FALSE | 7095 | 0000E040 | Ph A vars | TRUE | FALSE | 7095 | 0000E040 | Ph A vars | TRUE | FALSE | 7095 | 0000E040 | Ph A vars | TRUE | FALSE
7097 | 0000E041 | Ph B vars | FALSE | 7097 | 0000E041 | Ph B vars | TRUE | FALSE | 7097 | 0000E041 | Ph B vars | TRUE | FALSE | 7131 | 00001020 | Ex PV kWh C | FALSE | #N/A | 7097 | 0000E041 | Ph B vars | TRUE | FALSE | 7097 | 0000E041 | Ph B vars | TRUE | FALSE | 7097 | 0000E041 | Ph B vars | TRUE | FALSE | 7097 | 0000E041 | Ph B vars | TRUE | FALSE | 7097 | 0000E041 | Ph B vars | TRUE | FALSE | 7097 | 0000E041 | Ph B vars | TRUE | FALSE | 7097 | 0000E041 | Ph B vars | TRUE | FALSE | 7097 | 0000E041 | Ph B vars | TRUE | FALSE
7099 | 0000E042 | Ph C vars | FALSE | 7099 | 0000E042 | Ph C vars | TRUE | FALSE | 7099 | 0000E042 | Ph C vars | TRUE | FALSE | 7133 | 00001021 | Ex PV kWh B | FALSE | #N/A | 7099 | 0000E042 | Ph C vars | TRUE | FALSE | 7099 | 0000E042 | Ph C vars | TRUE | FALSE | 7099 | 0000E042 | Ph C vars | TRUE | FALSE | 7099 | 0000E042 | Ph C vars | TRUE | FALSE | 7099 | 0000E042 | Ph C vars | TRUE | FALSE | 7099 | 0000E042 | Ph C vars | TRUE | FALSE | 7099 | 0000E042 | Ph C vars | TRUE | FALSE | 7099 | 0000E042 | Ph C vars | TRUE | FALSE
7101 | 0000E050 | Ph A VA | FALSE | 7101 | 0000E050 | Ph A VA | TRUE | FALSE | 7101 | 0000E050 | Ph A VA | TRUE | FALSE | 7135 | 00001022 | Ex PV kWh C | FALSE | #N/A | 7101 | 0000E050 | Ph A VA | TRUE | FALSE | 7101 | 0000E050 | Ph A VA | TRUE | FALSE | 7101 | 0000E050 | Ph A VA | TRUE | FALSE | 7101 | 0000E050 | Ph A VA | TRUE | FALSE | 7101 | 0000E050 | Ph A VA | TRUE | FALSE | 7101 | 0000E050 | Ph A VA | TRUE | FALSE | 7101 | 0000E050 | Ph A VA | TRUE | FALSE | 7101 | 0000E050 | Ph A VA | TRUE | FALSE
7103 | 0000E051 | Ph B VA | FALSE | 7103 | 0000E051 | Ph B VA | TRUE | FALSE | 7103 | 0000E051 | Ph B VA | TRUE | FALSE | 7137 | 00000149 | Ex BT Total kVAr | FALSE | #N/A | 7103 | 0000E051 | Ph B VA | TRUE | FALSE | 7103 | 0000E051 | Ph B VA | TRUE | FALSE | 7103 | 0000E051 | Ph B VA | TRUE | FALSE | 7103 | 0000E051 | Ph B VA | TRUE | FALSE | 7103 | 0000E051 | Ph B VA | TRUE | FALSE | 7103 | 0000E051 | Ph B VA | TRUE | FALSE | 7103 | 0000E051 | Ph B VA | TRUE | FALSE | 7103 | 0000E051 | Ph B VA | TRUE | FALSE
7105 | 0000E052 | Ph C VA | FALSE | 7105 | 0000E052 | Ph C VA | TRUE | FALSE | 7105 | 0000E052 | Ph C VA | TRUE | FALSE | 7139 | 00001129 | Ex PV KVarh | FALSE | 18 | 7105 | 0000E052 | Ph C VA | TRUE | FALSE | 7105 | 0000E052 | Ph C VA | TRUE | FALSE | 7105 | 0000E052 | Ph C VA | TRUE | FALSE | 7105 | 0000E052 | Ph C VA | TRUE | FALSE | 7105 | 0000E052 | Ph C VA | TRUE | FALSE | 7105 | 0000E052 | Ph C VA | TRUE | FALSE | 7105 | 0000E052 | Ph C VA | TRUE | FALSE | 7105 | 0000E052 | Ph C VA | TRUE | FALSE
7107 | 0000E060 | Frequency | FALSE | 7107 | 0000E060 | Frequency | TRUE | FALSE | 7107 | 0000E060 | Frequency | TRUE | FALSE | 7141 | 00001149 | Ex Total kVAr | FALSE | #N/A | 7107 | 0000E060 | Frequency | TRUE | FALSE | 7107 | 0000E060 | Frequency | TRUE | FALSE | 7107 | 0000E060 | Frequency | TRUE | FALSE | 7107 | 0000E060 | Frequency | TRUE | FALSE | 7107 | 0000E060 | Frequency | TRUE | FALSE | 7107 | 0000E060 | Frequency | TRUE | FALSE | 7107 | 0000E060 | Frequency | TRUE | FALSE | 7107 | 0000E060 | Frequency | TRUE | FALSE
7109 | 0000E024 | Angle VTA&VTB | FALSE | 7109 | 0000E024 | Angle VTA&VTB | TRUE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | TRUE | FALSE | 7143 | 00008020 | Ex PV kWp A Time | FALSE | #N/A | 7109 | 0000E024 | Angle VTA&VTB | TRUE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | TRUE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | TRUE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | TRUE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | TRUE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | TRUE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | TRUE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | TRUE | FALSE
7111 | 0000E025 | Angle VTA&VTC | FALSE | 7111 | 0000E025 | Angle VTA&VTC | TRUE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | TRUE | FALSE | 7147 | 00008021 | Ex PV kWp B Time | FALSE | #N/A | 7111 | 0000E025 | Angle VTA&VTC | TRUE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | TRUE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | TRUE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | TRUE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | TRUE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | TRUE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | TRUE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | TRUE | FALSE
7113 | 0000E026 | Power Factor | FALSE | 7113 | 0000E026 | Power Factor | TRUE | FALSE | 7113 | 0000E026 | Power Factor | TRUE | FALSE | 7151 | 00008022 | Ex PV kWp C Time | FALSE | #N/A | 7113 | 0000E026 | Power Factor | TRUE | FALSE | 7113 | 0000E026 | Power Factor | TRUE | FALSE | 7113 | 0000E026 | Power Factor | TRUE | FALSE | 7113 | 0000E026 | Power Factor | TRUE | FALSE | 7113 | 0000E026 | Power Factor | TRUE | FALSE | 7113 | 0000E026 | Power Factor | TRUE | FALSE | 7113 | 0000E026 | Power Factor | TRUE | FALSE | 7113 | 0000E026 | Power Factor | TRUE | FALSE
7115 | 00000200 | Im kWh RateA | 57 | 7115 | 00000200 | Im kWh RateA | TRUE | 57 | 7115 | 00000200 | Im kWh RateA | TRUE | 57 | [5 empty] | 7115 | 00000200 | Im kWh RateA | TRUE | 57 | 7115 | 00000200 | Im kWh RateA | TRUE | 57 | 7115 | 00000200 | Im kWh RateA | TRUE | 57 | 7115 | 00000200 | Im kWh RateA | TRUE | 57 | 7115 | 00000200 | Im kWh RateA | TRUE | 57 | 7115 | 00000200 | Im kWh RateA | TRUE | 57 | 7115 | 00000200 | Im kWh RateA | TRUE | 57 | 7115 | 00000200 | Im kWh RateA | TRUE | 57
7117 | 00000201 | Im kWh RateB | 58 | 7117 | 00000201 | Im kWh RateB | TRUE | 58 | 7117 | 00000201 | Im kWh RateB | TRUE | 58 | [5 empty] | 7117 | 00000201 | Im kWh RateB | TRUE | 58 | 7117 | 00000201 | Im kWh RateB | TRUE | 58 | 7117 | 00000201 | Im kWh RateB | TRUE | 58 | 7117 | 00000201 | Im kWh RateB | TRUE | 58 | 7117 | 00000201 | Im kWh RateB | TRUE | 58 | 7117 | 00000201 | Im kWh RateB | TRUE | 58 | 7117 | 00000201 | Im kWh RateB | TRUE | 58 | 7117 | 00000201 | Im kWh RateB | TRUE | 58
7119 | 00000202 | Im kWh RateC | 59 | 7119 | 00000202 | Im kWh RateC | TRUE | 59 | 7119 | 00000202 | Im kWh RateC | TRUE | 59 | [5 empty] | 7119 | 00000202 | Im kWh RateC | TRUE | 59 | 7119 | 00000202 | Im kWh RateC | TRUE | 59 | 7119 | 00000202 | Im kWh RateC | TRUE | 59 | 7119 | 00000202 | Im kWh RateC | TRUE | 59 | 7119 | 00000202 | Im kWh RateC | TRUE | 59 | 7119 | 00000202 | Im kWh RateC | TRUE | 59 | 7119 | 00000202 | Im kWh RateC | TRUE | 59 | 7119 | 00000202 | Im kWh RateC | TRUE | 59
7121 | 00001200 | Im Max kW A | FALSE | 7121 | 00001200 | Im Max kW A | TRUE | FALSE | 7121 | 00001200 | Im Max kW A | TRUE | FALSE | [5 empty] | 7121 | 00001200 | Im Max kW A | TRUE | FALSE | 7121 | 00001200 | Im Max kW A | TRUE | FALSE | 7121 | 00001200 | Im Max kW A | TRUE | FALSE | 7121 | 00001200 | Im Max kW A | TRUE | FALSE | 7121 | 00001200 | Im Max kW A | TRUE | FALSE | 7121 | 00001200 | Im Max kW A | TRUE | FALSE | 7121 | 00001200 | Im Max kW A | TRUE | FALSE | 7121 | 00001200 | Im Max kW A | TRUE | FALSE
7123 | 00001201 | Im Max kW B | FALSE | 7123 | 00001201 | Im Max kW B | TRUE | FALSE | 7123 | 00001201 | Im Max kW B | TRUE | FALSE | [5 empty] | 7123 | 00001201 | Im Max kW B | TRUE | FALSE | 7123 | 00001201 | Im Max kW B | TRUE | FALSE | 7123 | 00001201 | Im Max kW B | TRUE | FALSE | 7123 | 00001201 | Im Max kW B | TRUE | FALSE | 7123 | 00001201 | Im Max kW B | TRUE | FALSE | 7123 | 00001201 | Im Max kW B | TRUE | FALSE | 7123 | 00001201 | Im Max kW B | TRUE | FALSE | 7123 | 00001201 | Im Max kW B | TRUE | FALSE
7125 | 00001202 | Im Max kW C | FALSE | 7125 | 00001202 | Im Max kW C | TRUE | FALSE | 7125 | 00001202 | Im Max kW C | TRUE | FALSE | [5 empty] | 7125 | 00001202 | Im Max kW C | TRUE | FALSE | 7125 | 00001202 | Im Max kW C | TRUE | FALSE | 7125 | 00001202 | Im Max kW C | TRUE | FALSE | 7125 | 00001202 | Im Max kW C | TRUE | FALSE | 7125 | 00001202 | Im Max kW C | TRUE | FALSE | 7125 | 00001202 | Im Max kW C | TRUE | FALSE | 7125 | 00001202 | Im Max kW C | TRUE | FALSE | 7125 | 00001202 | Im Max kW C | TRUE | FALSE
7127 | 00000369 | Im Total kVArh | 63 | 7127 | 00000369 | Im Total kVArh | TRUE | 63 | 7127 | 00000369 | Im Total kVArh | TRUE | 63 | [5 empty] | 7127 | 00000369 | Im Total kVArh | TRUE | 63 | 7127 | 00000369 | Im Total kVArh | TRUE | 63 | 7127 | 00000369 | Im Total kVArh | TRUE | 63 | 7127 | 00000369 | Im Total kVArh | TRUE | 63 | 7127 | 00000369 | Im Total kVArh | TRUE | 63 | 7127 | 00000369 | Im Total kVArh | TRUE | 63 | 7127 | 00000369 | Im Total kVArh | TRUE | 63 | 7127 | 00000369 | Im Total kVArh | TRUE | 63
7129 | 00000360 | Im kVArh A | FALSE | 7129 | 00000360 | Im kVArh A | TRUE | FALSE | 7129 | 00000360 | Im kVArh A | TRUE | FALSE | [5 empty] | 7129 | 00000360 | Im kVArh A | TRUE | FALSE | 7129 | 00000360 | Im kVArh A | TRUE | FALSE | 7129 | 00000360 | Im kVArh A | TRUE | FALSE | 7129 | 00000360 | Im kVArh A | TRUE | FALSE | 7129 | 00000360 | Im kVArh A | TRUE | FALSE | 7129 | 00000360 | Im kVArh A | TRUE | FALSE | 7129 | 00000360 | Im kVArh A | TRUE | FALSE | 7129 | 00000360 | Im kVArh A | TRUE | FALSE
7131 | 00000361 | Im kVArh B | FALSE | 7131 | 00000361 | Im kVArh B | TRUE | FALSE | 7131 | 00000361 | Im kVArh B | TRUE | FALSE | [5 empty] | 7131 | 00000361 | Im kVArh B | TRUE | FALSE | 7131 | 00000361 | Im kVArh B | TRUE | FALSE | 7131 | 00000361 | Im kVArh B | TRUE | FALSE | 7131 | 00000361 | Im kVArh B | TRUE | FALSE | 7131 | 00000361 | Im kVArh B | TRUE | FALSE | 7131 | 00000361 | Im kVArh B | TRUE | FALSE | 7131 | 00000361 | Im kVArh B | TRUE | FALSE | 7131 | 00000361 | Im kVArh B | TRUE | FALSE
7133 | 00000362 | Im kVArh C | FALSE | 7133 | 00000362 | Im kVArh C | TRUE | FALSE | 7133 | 00000362 | Im kVArh C | TRUE | FALSE | [5 empty] | 7133 | 00000362 | Im kVArh C | TRUE | FALSE | 7133 | 00000362 | Im kVArh C | TRUE | FALSE | 7133 | 00000362 | Im kVArh C | TRUE | FALSE | 7133 | 00000362 | Im kVArh C | TRUE | FALSE | 7133 | 00000362 | Im kVArh C | TRUE | FALSE | 7133 | 00000362 | Im kVArh C | TRUE | FALSE | 7133 | 00000362 | Im kVArh C | TRUE | FALSE | 7133 | 00000362 | Im kVArh C | TRUE | FALSE
7135 | 00001300 | Im Max kVArh A | FALSE | 7135 | 00001300 | Im Max kVArh A | TRUE | FALSE | 7135 | 00001300 | Im Max kVArh A | TRUE | FALSE | [5 empty] | 7135 | 00001300 | Im Max kVArh A | TRUE | FALSE | 7135 | 00001300 | Im Max kVArh A | TRUE | FALSE | 7135 | 00001300 | Im Max kVArh A | TRUE | FALSE | 7135 | 00001300 | Im Max kVArh A | TRUE | FALSE | 7135 | 00001300 | Im Max kVArh A | TRUE | FALSE | 7135 | 00001300 | Im Max kVArh A | TRUE | FALSE | 7135 | 00001300 | Im Max kVArh A | TRUE | FALSE | 7135 | 00001300 | Im Max kVArh A | TRUE | FALSE
7137 | 00001301 | Im Max kVArh B | FALSE | 7137 | 00001301 | Im Max kVArh B | TRUE | FALSE | 7137 | 00001301 | Im Max kVArh B | TRUE | FALSE | [5 empty] | 7137 | 00001301 | Im Max kVArh B | TRUE | FALSE | 7137 | 00001301 | Im Max kVArh B | TRUE | FALSE | 7137 | 00001301 | Im Max kVArh B | TRUE | FALSE | 7137 | 00001301 | Im Max kVArh B | TRUE | FALSE | 7137 | 00001301 | Im Max kVArh B | TRUE | FALSE | 7137 | 00001301 | Im Max kVArh B | TRUE | FALSE | 7137 | 00001301 | Im Max kVArh B | TRUE | FALSE | 7137 | 00001301 | Im Max kVArh B | TRUE | FALSE
7139 | 00001302 | Im Max kVArh C | FALSE | 7139 | 00001302 | Im Max kVArh C | TRUE | FALSE | 7139 | 00001302 | Im Max kVArh C | TRUE | FALSE | [5 empty] | 7139 | 00001302 | Im Max kVArh C | TRUE | FALSE | 7139 | 00001302 | Im Max kVArh C | TRUE | FALSE | 7139 | 00001302 | Im Max kVArh C | TRUE | FALSE | 7139 | 00001302 | Im Max kVArh C | TRUE | FALSE | 7139 | 00001302 | Im Max kVArh C | TRUE | FALSE | 7139 | 00001302 | Im Max kVArh C | TRUE | FALSE | 7139 | 00001302 | Im Max kVArh C | TRUE | FALSE | 7139 | 00001302 | Im Max kVArh C | TRUE | FALSE
7141 | 00000340 | Im kVArh-CumA | FALSE | 7141 | 00000340 | Im kVArh-CumA | TRUE | FALSE | 7141 | 00000340 | Im kVArh-CumA | TRUE | FALSE | [5 empty] | 7141 | 00000340 | Im kVArh-CumA | TRUE | FALSE | 7141 | 00000340 | Im kVArh-CumA | TRUE | FALSE | 7141 | 00000340 | Im kVArh-CumA | TRUE | FALSE | 7141 | 00000340 | Im kVArh-CumA | TRUE | FALSE | 7141 | 00000340 | Im kVArh-CumA | TRUE | FALSE | 7141 | 00000340 | Im kVArh-CumA | TRUE | FALSE | 7141 | 00000340 | Im kVArh-CumA | TRUE | FALSE | 7141 | 00000340 | Im kVArh-CumA | TRUE | FALSE
7143 | 00000341 | Im kVArh-CumB | FALSE | 7143 | 00000341 | Im kVArh-CumB | TRUE | FALSE | 7143 | 00000341 | Im kVArh-CumB | TRUE | FALSE | [5 empty] | 7143 | 00000341 | Im kVArh-CumB | TRUE | FALSE | 7143 | 00000341 | Im kVArh-CumB | TRUE | FALSE | 7143 | 00000341 | Im kVArh-CumB | TRUE | FALSE | 7143 | 00000341 | Im kVArh-CumB | TRUE | FALSE | 7143 | 00000341 | Im kVArh-CumB | TRUE | FALSE | 7143 | 00000341 | Im kVArh-CumB | TRUE | FALSE | 7143 | 00000341 | Im kVArh-CumB | TRUE | FALSE | 7143 | 00000341 | Im kVArh-CumB | TRUE | FALSE
7145 | 00000342 | Im kVArh-CumC | FALSE | 7145 | 00000342 | Im kVArh-CumC | TRUE | FALSE | 7145 | 00000342 | Im kVArh-CumC | TRUE | FALSE | [5 empty] | 7145 | 00000342 | Im kVArh-CumC | TRUE | FALSE | 7145 | 00000342 | Im kVArh-CumC | TRUE | FALSE | 7145 | 00000342 | Im kVArh-CumC | TRUE | FALSE | 7145 | 00000342 | Im kVArh-CumC | TRUE | FALSE | 7145 | 00000342 | Im kVArh-CumC | TRUE | FALSE | 7145 | 00000342 | Im kVArh-CumC | TRUE | FALSE | 7145 | 00000342 | Im kVArh-CumC | TRUE | FALSE | 7145 | 00000342 | Im kVArh-CumC | TRUE | FALSE
7147 | 00000249 | Im BT Total kWh | FALSE | 7147 | 00000249 | Im BT Total kWh | TRUE | FALSE | 7147 | 00000249 | Im BT Total kWh | TRUE | FALSE | [5 empty] | 7147 | 00000249 | Im BT Total kWh | TRUE | FALSE | 7147 | 00000249 | Im BT Total kWh | TRUE | FALSE | 7147 | 00000249 | Im BT Total kWh | TRUE | FALSE | 7147 | 00000249 | Im BT Total kWh | TRUE | FALSE | 7147 | 00000249 | Im BT Total kWh | TRUE | 73 | 7147 | 00000249 | Im BT Total kWh | TRUE | FALSE | 7147 | 00000249 | Im BT Total kWh | TRUE | FALSE | 7147 | 00000249 | Im BT Total kWh | TRUE | FALSE
7149 | 00000240 | Im BT kWh A | FALSE | 7149 | 00000240 | Im BT kWh A | TRUE | FALSE | 7149 | 00000240 | Im BT kWh A | TRUE | FALSE | [5 empty] | 7149 | 00000240 | Im BT kWh A | TRUE | FALSE | 7149 | 00000240 | Im BT kWh A | TRUE | FALSE | 7149 | 00000240 | Im BT kWh A | TRUE | FALSE | 7149 | 00000240 | Im BT kWh A | TRUE | FALSE | 7149 | 00000240 | Im BT kWh A | TRUE | 74 | 7149 | 00000240 | Im BT kWh A | TRUE | FALSE | 7149 | 00000240 | Im BT kWh A | TRUE | FALSE | 7149 | 00000240 | Im BT kWh A | TRUE | FALSE
7151 | 00000241 | Im BT kWh B | FALSE | 7151 | 00000241 | Im BT kWh B | TRUE | FALSE | 7151 | 00000241 | Im BT kWh B | TRUE | FALSE | [5 empty] | 7151 | 00000241 | Im BT kWh B | TRUE | FALSE | 7151 | 00000241 | Im BT kWh B | TRUE | FALSE | 7151 | 00000241 | Im BT kWh B | TRUE | FALSE | 7151 | 00000241 | Im BT kWh B | TRUE | FALSE | 7151 | 00000241 | Im BT kWh B | TRUE | 75 | 7151 | 00000241 | Im BT kWh B | TRUE | FALSE | 7151 | 00000241 | Im BT kWh B | TRUE | FALSE | 7151 | 00000241 | Im BT kWh B | TRUE | FALSE
7153 | 00000242 | Im BT kWh C | FALSE | 7153 | 00000242 | Im BT kWh C | TRUE | FALSE | 7153 | 00000242 | Im BT kWh C | TRUE | FALSE | [5 empty] | 7153 | 00000242 | Im BT kWh C | TRUE | FALSE | 7153 | 00000242 | Im BT kWh C | TRUE | FALSE | 7153 | 00000242 | Im BT kWh C | TRUE | FALSE | 7153 | 00000242 | Im BT kWh C | TRUE | FALSE | 7153 | 00000242 | Im BT kWh C | TRUE | 76 | 7153 | 00000242 | Im BT kWh C | TRUE | FALSE | 7153 | 00000242 | Im BT kWh C | TRUE | FALSE | 7153 | 00000242 | Im BT kWh C | TRUE | FALSE
7155 | 00001220 | Im PV kW A | FALSE | 7155 | 00001220 | Im PV kW A | TRUE | FALSE | 7155 | 00001220 | Im PV kW A | TRUE | FALSE | [5 empty] | 7155 | 00001220 | Im PV kW A | TRUE | FALSE | 7155 | 00001220 | Im PV kW A | TRUE | FALSE | 7155 | 00001220 | Im PV kW A | TRUE | FALSE | 7155 | 00001220 | Im PV kW A | TRUE | FALSE | 7155 | 00001220 | Im PV kW A | TRUE | FALSE | 7155 | 00001220 | Im PV kW A | TRUE | FALSE | 7155 | 00001220 | Im PV kW A | TRUE | FALSE | 7155 | 00001220 | Im PV kW A | TRUE | FALSE
7157 | 00001221 | Im PV kW B | FALSE | 7157 | 00001221 | Im PV kW B | TRUE | FALSE | 7157 | 00001221 | Im PV kW B | TRUE | FALSE | [5 empty] | 7157 | 00001221 | Im PV kW B | TRUE | FALSE | 7157 | 00001221 | Im PV kW B | TRUE | FALSE | 7157 | 00001221 | Im PV kW B | TRUE | FALSE | 7157 | 00001221 | Im PV kW B | TRUE | FALSE | 7157 | 00001221 | Im PV kW B | TRUE | FALSE | 7157 | 00001221 | Im PV kW B | TRUE | FALSE | 7157 | 00001221 | Im PV kW B | TRUE | FALSE | 7157 | 00001221 | Im PV kW B | TRUE | FALSE
7159 | 00001222 | Im PV kW C | FALSE | 7159 | 00001222 | Im PV kW C | TRUE | FALSE | 7159 | 00001222 | Im PV kW C | TRUE | FALSE | [5 empty] | 7159 | 00001222 | Im PV kW C | TRUE | FALSE | 7159 | 00001222 | Im PV kW C | TRUE | FALSE | 7159 | 00001222 | Im PV kW C | TRUE | FALSE | 7159 | 00001222 | Im PV kW C | TRUE | FALSE | 7159 | 00001222 | Im PV kW C | TRUE | FALSE | 7159 | 00001222 | Im PV kW C | TRUE | FALSE | 7159 | 00001222 | Im PV kW C | TRUE | FALSE | 7159 | 00001222 | Im PV kW C | TRUE | FALSE
7161 | 00001240 | Im kW-Cum A | FALSE | 7161 | 00001240 | Im kW-Cum A | TRUE | FALSE | 7161 | 00001240 | Im kW-Cum A | TRUE | FALSE | [5 empty] | 7161 | 00001240 | Im kW-Cum A | TRUE | FALSE | 7161 | 00001240 | Im kW-Cum A | TRUE | FALSE | 7161 | 00001240 | Im kW-Cum A | TRUE | FALSE | 7161 | 00001240 | Im kW-Cum A | TRUE | FALSE | 7161 | 00001240 | Im kW-Cum A | TRUE | FALSE | 7161 | 00001240 | Im kW-Cum A | TRUE | FALSE | 7161 | 00001240 | Im kW-Cum A | TRUE | FALSE | 7161 | 00001240 | Im kW-Cum A | TRUE | FALSE
7163 | 00001241 | Im kW-Cum B | FALSE | 7163 | 00001241 | Im kW-Cum B | TRUE | FALSE | 7163 | 00001241 | Im kW-Cum B | TRUE | FALSE | [5 empty] | 7163 | 00001241 | Im kW-Cum B | TRUE | FALSE | 7163 | 00001241 | Im kW-Cum B | TRUE | FALSE | 7163 | 00001241 | Im kW-Cum B | TRUE | FALSE | 7163 | 00001241 | Im kW-Cum B | TRUE | FALSE | 7163 | 00001241 | Im kW-Cum B | TRUE | FALSE | 7163 | 00001241 | Im kW-Cum B | TRUE | FALSE | 7163 | 00001241 | Im kW-Cum B | TRUE | FALSE | 7163 | 00001241 | Im kW-Cum B | TRUE | FALSE
7165 | 00001242 | Im kW-Cum C | FALSE | 7165 | 00001242 | Im kW-Cum C | TRUE | FALSE | 7165 | 00001242 | Im kW-Cum C | TRUE | FALSE | [5 empty] | 7165 | 00001242 | Im kW-Cum C | TRUE | FALSE | 7165 | 00001242 | Im kW-Cum C | TRUE | FALSE | 7165 | 00001242 | Im kW-Cum C | TRUE | FALSE | 7165 | 00001242 | Im kW-Cum C | TRUE | FALSE | 7165 | 00001242 | Im kW-Cum C | TRUE | FALSE | 7165 | 00001242 | Im kW-Cum C | TRUE | FALSE | 7165 | 00001242 | Im kW-Cum C | TRUE | FALSE | 7165 | 00001242 | Im kW-Cum C | TRUE | FALSE
7167 | 00000149 | Im BT Total kVArh | FALSE | 7167 | 00000149 | Im BT Total kVArh | TRUE | FALSE | 7167 | 00001349 | Im BT Total kVAr | FALSE | FALSE | [5 empty] | 7167 | 00000149 | Im BT Total kVArh | TRUE | FALSE | 7167 | 00000149 | Im BT Total kVArh | TRUE | FALSE | 7167 | 00000149 | Im BT Total kVArh | TRUE | FALSE | 7167 | 00000149 | Im BT Total kVArh | TRUE | FALSE | 7167 | 00000149 | Im BT Total kVArh | TRUE | FALSE | 7167 | 00000149 | Im BT Total kVArh | TRUE | FALSE | 7167 | 00000149 | Im BT Total kVArh | TRUE | FALSE | 7167 | 00001349 | Im BT Total kVAr | FALSE | FALSE
7169 | 00000329 | Im PV kVAr | FALSE | 7169 | 00000329 | Im PV kVAr | TRUE | FALSE | 7169 | 00000329 | Im PV kVAr | TRUE | FALSE | [5 empty] | 7169 | 00000329 | Im PV kVAr | TRUE | FALSE | 7169 | 00000329 | Im PV kVAr | TRUE | FALSE | 7169 | 00000329 | Im PV kVAr | TRUE | FALSE | 7169 | 00000329 | Im PV kVAr | TRUE | FALSE | 7169 | 00000329 | Im PV kVAr | TRUE | FALSE | 7169 | 00000329 | Im PV kVAr | TRUE | FALSE | 7169 | 00000329 | Im PV kVAr | TRUE | FALSE | 7169 | 00000329 | Im PV kVAr | TRUE | FALSE
7171 | 00000369 | Im kVAr-Cum | FALSE | 7171 | 00000369 | Im kVAr-Cum | TRUE | FALSE | 7171 | 00000369 | Im kVAr-Cum | TRUE | FALSE | [5 empty] | 7171 | 00000369 | Im kVAr-Cum | TRUE | FALSE | 7171 | 00000369 | Im kVAr-Cum | TRUE | FALSE | 7171 | 00000369 | Im kVAr-Cum | TRUE | FALSE | 7171 | 00000369 | Im kVAr-Cum | TRUE | FALSE | 7171 | 00000369 | Im kVAr-Cum | TRUE | FALSE | 7171 | 00000369 | Im kVAr-Cum | TRUE | FALSE | 7171 | 00000369 | Im kVAr-Cum | TRUE | FALSE | 7171 | 00000369 | Im kVAr-Cum | TRUE | FALSE
7173 | 00000269 | Im Total kWh | #N/A | 7173 | 00000269 | Im Total kWh | TRUE | #N/A | 7173 | 00000269 | Im Total kWh | TRUE | #N/A | [5 empty] | 7173 | 00000269 | Im Total kWh | TRUE | 86 | 7173 | 00000269 | Im Total kWh | TRUE | 86 | 7173 | 00000269 | Im Total kWh | TRUE | 86 | 7173 | 00000269 | Im Total kWh | TRUE | 86 | 7173 | 00000269 | Im Total kWh | TRUE | 86 | 7173 | 00000269 | Im Total kWh | TRUE | 86 | 7173 | 00000269 | Im Total kWh | TRUE | 86 | 7173 | 00000269 | Im Total kWh | TRUE | 86
7175 | 00001129 | Ex PV KVarh | 89 | 7175 | 00001129 | Ex PV KVarh | TRUE | 89 | 7175 | 00001129 | Ex PV KVarh | TRUE | 89 | [5 empty] | 7175 | 00001129 | Ex PV KVarh | TRUE | #N/A | 7175 | 00001129 | Ex PV KVarh | TRUE | #N/A | 7175 | 00001129 | Ex PV KVarh | TRUE | FALSE | 7175 | 00001129 | Ex PV KVarh | TRUE | #N/A | 7175 | 00001129 | Ex PV KVarh | TRUE | #N/A | 7175 | 00001129 | Ex PV KVarh | TRUE | #N/A | 7175 | 00001129 | Ex PV KVarh | TRUE | FALSE | 7175 | 00001129 | Ex PV KVarh | TRUE | 88
7177 | 00008129 | Ex PV KVarh Time | #N/A | 7177 | 00008129 | Ex PV KVarh Time | TRUE | #N/A | 7177 | 00001129 | Ex PV KVarh | FALSE | #N/A | [5 empty] | 7250 | 00008129 | Ex PV KVarh Time | TRUE | #N/A | 7177 | 00008129 | Ex PV KVarh Time | TRUE | #N/A | 7177 | 00008129 | Ex PV KVarh Time | TRUE | #N/A | 7177 | 00008129 | Ex PV KVarh Time | TRUE | #N/A | 7177 | 00008129 | Ex PV KVarh Time | TRUE | #N/A | 7177 | 00008129 | Ex PV KVarh Time | TRUE | #N/A | 7177 | 00008129 | Ex PV KVarh Time | TRUE | #N/A | 7177 | 00001129 | Ex PV KVarh | FALSE | #N/A
7181 | 00001149 | Ex Total kVAr | 90 | 7181 | 00001149 | Ex Total kVAr | TRUE | FALSE | 7179 | 00008129 | Ex PV KVarh Time | FALSE | #N/A | [5 empty] | 7181 | 00001149 | Ex Total kVAr | TRUE | FALSE | 7181 | 00001149 | Ex Total kVAr | TRUE | FALSE | 7181 | 00001149 | Ex Total kVAr | TRUE | FALSE | 7181 | 00001149 | Ex Total kVAr | TRUE | FALSE | 7181 | 00001149 | Ex Total kVAr | TRUE | FALSE | 7181 | 00001149 | Ex Total kVAr | TRUE | FALSE | 7181 | 00001149 | Ex Total kVAr | TRUE | FALSE | 7179 | 00008129 | Ex PV KVarh Time | FALSE | #N/A
7183 | 0000F032 | NB Reset | 91 | 7183 | 0000F032 | NB Reset | TRUE | FALSE | 7181 | 00008129 | Ex PV KVarh Time | FALSE | FALSE | [5 empty] | 7183 | 0000F032 | NB Reset | TRUE | #N/A | 7183 | 0000F032 | NB Reset | TRUE | #N/A | 7183 | 0000F032 | NB Reset | TRUE | FALSE | 7183 | 0000F032 | NB Reset | TRUE | #N/A | 7183 | 0000F032 | NB Reset | TRUE | #N/A | 7183 | 0000F032 | NB Reset | TRUE | #N/A | 7183 | 0000F032 | NB Reset | TRUE | FALSE | 7181 | 00008129 | Ex PV KVarh Time | FALSE | 87
7185 | 00008020 | Ex PV kW A Time | #N/A | 7185 | 00008020 | Ex PV kW A Time | TRUE | #N/A | 7183 | 00001149 | Ex Total kVAr | FALSE | FALSE | [5 empty] | 7185 | 00008020 | Ex PV kW A Time | TRUE | #N/A | 7185 | 00008020 | Ex PV kW A Time | TRUE | #N/A | 7185 | 00008020 | Ex PV kW A Time | TRUE | #N/A | 7185 | 00008020 | Ex PV kW A Time | TRUE | #N/A | 7185 | 00008020 | Ex PV kW A Time | TRUE | #N/A | 7185 | 00008020 | Ex PV kW A Time | TRUE | #N/A | 7185 | 00008020 | Ex PV kW A Time | TRUE | #N/A | 7183 | 00001149 | Ex Total kVAr | FALSE | 89
7189 | 00008021 | Ex PV kW B Time | #N/A | 7189 | 00008021 | Ex PV kW B Time | TRUE | #N/A | 7185 | 0000F032 | NB Reset | FALSE | #N/A | [5 empty] | 7189 | 00008021 | Ex PV kW B Time | TRUE | #N/A | 7189 | 00008021 | Ex PV kW B Time | TRUE | #N/A | 7189 | 00008021 | Ex PV kW B Time | TRUE | #N/A | 7189 | 00008021 | Ex PV kW B Time | TRUE | #N/A | 7189 | 00008021 | Ex PV kW B Time | TRUE | #N/A | 7189 | 00008021 | Ex PV kW B Time | TRUE | #N/A | 7189 | 00008021 | Ex PV kW B Time | TRUE | #N/A | 7185 | 0000F032 | NB Reset | FALSE | #N/A
7193 | 00008022 | Ex PV kW C Time | #N/A | 7193 | 00008022 | Ex PV kW C Time | TRUE | #N/A | 7187 | 00008020 | Ex PV kW A Time | FALSE | FALSE | [5 empty] | 7193 | 00008022 | Ex PV kW C Time | TRUE | #N/A | 7193 | 00008022 | Ex PV kW C Time | TRUE | #N/A | 7193 | 00008022 | Ex PV kW C Time | TRUE | #N/A | 7193 | 00008022 | Ex PV kW C Time | TRUE | #N/A | 7193 | 00008022 | Ex PV kW C Time | TRUE | #N/A | 7193 | 00008022 | Ex PV kW C Time | TRUE | #N/A | 7193 | 00008022 | Ex PV kW C Time | TRUE | #N/A | 7187 | 00008020 | Ex PV kW A Time | FALSE | #N/A
[9 empty] | 7191 | 00008021 | Ex PV kW B Time | FALSE | #N/A | [5 empty] | 7207 | 0000F092 | Check_LCD | FALSE | #N/A | [15 empty] | 7300 | 0000F03D | Date_time | FALSE | #N/A | [10 empty] | 7191 | 00008021 | Ex PV kW B Time | FALSE | #N/A
[9 empty] | 7195 | 00008022 | Ex PV kW C Time | FALSE | #N/A | [5 empty] | 7209 | 0000F032 | Count_reset | FALSE | #N/A | [15 empty] | 7400 | 0000FC00 | date_to_reset_meter | FALSE | #N/A | [10 empty] | 7195 | 00008022 | Ex PV kW C Time | FALSE | #N/A
[9 empty] | 7199 | 0000FC00 | DT of Reset | FALSE | #N/A | [5 empty] | 7300 | 0000F03D | Date_time | FALSE | #N/A | [15 empty] | 7207 | 0000F092 | check_lcd | FALSE | #N/A | [10 empty] | 7199 | 0000FC00 | DT of Reset | FALSE | #N/A
[19 empty] | 7400 | 0000FC00 | Date_Reset_meter |  | #N/A | [15 empty] | 7209 | 0000F032 | count_reset | FALSE | #N/A
[39 empty] | 7251 | 00000260 | Im total KWh Rate A | FALSE | #N/A
[39 empty] | 7253 | 00000261 | Im total KWh Rate B | FALSE | #N/A
[39 empty] | 7255 | 00000262 | Im total KWh Rate C | FALSE | #N/A
[39 empty] | 7257 | 00000269 | Im total KWh 2 | FALSE | #N/A

## Sheet1
7001 | 0000E033 | Inst kW | 0 | #N/A | 0000F010 | Previous DD-MM-YY of Reading
7003 | 0000E043 | Inst kVAr | 1 | #N/A | 0000F011 | Previous Time of Reading
7005 | 00000069 | Ex Total kWh | 2 | #N/A | 0000FC00 | Previous DD-MM-YY : Time of Reset
7007 | 00000000 | Ex kWh RateA | 3 | #N/A | 0000F032 | PreviousTimes of Reset
7009 | 00000001 | Ex kWh RateB | 4 | #N/A | 00000049 | Previous kWh Total Reading(Reset)
7011 | 00000002 | Ex kWh RateC | 5 | #N/A | 00000040 | Previous kWh Rate A Reading(Reset)
7013 | 00001000 | Ex Max kW A | FALSE | #N/A | 00000041 | Previous kWh Rate B Reading(Reset)
7015 | 00001001 | Ex Max kW B | FALSE | #N/A | 00000042 | Previous kWh Rate C Reading(Reset)
7017 | 00001002 | Ex Max kW C | FALSE | #N/A | 00001020 | Previous kWp Rate A Reading(Reset)
7019 | 00001040 | Ex kW-Cum A | FALSE | Previous Comulative kWh-Rate A Reading | 00001021 | Previous kWp Rate B Reading(Reset)
7021 | 00001041 | Ex kW-Cum B | FALSE | Previous Comulative kWh-Rate B Reading | 00001022 | Previous kWp Rate C Reading(Reset)
7023 | 00001042 | Ex kW-Cum C | FALSE | Previous Comulative kWh-Rate C Reading | 00001040 | Previous Comulative kWh-Rate A Reading
7025 | 00000169 | Ex Total kVArh | 12 | #N/A | 00001041 | Previous Comulative kWh-Rate B Reading
7027 | 00000160 | Ex kVArh A | FALSE | #N/A | 00001042 | Previous Comulative kWh-Rate C Reading
7029 | 00000161 | Ex kVArh B | FALSE | #N/A | 00000149 | Previous total of kVarh total Reading(Reset)
7031 | 00000162 | Ex kVArh C | FALSE | #N/A | 00001129 | Previous kVar demand Total Reading(Reset)
7033 | 00001100 | Ex Max kVArh A | FALSE | #N/A | 00001149 | Previous Comulative kVarh demand Total Reading(Reset)
7035 | 00001101 | Ex Max kVArh B | FALSE | #N/A
7037 | 00001102 | Ex Max kVArh C | FALSE | #N/A
7039 | 00000140 | Ex kVArh-Cum A | FALSE | #N/A
7041 | 00000141 | Ex kVArh-Cum B | FALSE | #N/A
7043 | 00000142 | Ex kVArh-Cum C | FALSE | #N/A
7045 | 00000049 | Ex BT Total kWh | 22 | Previous kWh Total Reading(Reset)
7047 | 00000040 | Ex BT kWhA | 23 | Previous kWh Rate A Reading(Reset)
7049 | 00000041 | Ex BT kWhB | 24 | Previous kWh Rate B Reading(Reset)
7051 | 00000042 | Ex BT kWhC | 25 | Previous kWh Rate C Reading(Reset)
7053 | 00001020 | Ex PV kW A | FALSE | Previous kWp Rate A Reading(Reset)
7055 | 00001021 | Ex PV kW B | FALSE | Previous kWp Rate B Reading(Reset)
7057 | 00001022 | Ex PV kW C | FALSE | Previous kWp Rate C Reading(Reset)
7059 | 00001040 | Ex kW-Cum A | 29 | Previous Comulative kWh-Rate A Reading
7061 | 00001041 | Ex kW-Cum B | 30 | Previous Comulative kWh-Rate B Reading
7063 | 00001042 | Ex kW-Cum C | 31 | Previous Comulative kWh-Rate C Reading
7065 | 00000149 | Ex BT Total kVAr | 32 | Previous total of kVarh total Reading(Reset)
7067 | 00000129 | Ex PV kVAr | FALSE | #N/A
7069 | 00000169 | Ex kVAr-Cum | FALSE | #N/A
7071 | 0000E000 | Ph A Volt | FALSE | #N/A
7073 | 0000E001 | Ph B Volt | FALSE | #N/A
7075 | 0000E002 | Ph C Volt | FALSE | #N/A
7077 | 0000E010 | Ph A Curr | FALSE | #N/A
7079 | 0000E011 | Ph B Curr | FALSE | #N/A
7081 | 0000E012 | Ph C Curr | FALSE | #N/A
7083 | 0000E020 | Ph A angle | FALSE | #N/A
7085 | 0000E021 | Ph B angle | FALSE | #N/A
7087 | 0000E022 | Ph C angle | FALSE | #N/A
7089 | 0000E030 | Ph A Watts | FALSE | #N/A
7091 | 0000E031 | Ph B Watts | FALSE | #N/A
7093 | 0000E032 | Ph C Watts | FALSE | #N/A
7095 | 0000E040 | Ph A vars | FALSE | #N/A
7097 | 0000E041 | Ph B vars | FALSE | #N/A
7099 | 0000E042 | Ph C vars | FALSE | #N/A
7101 | 0000E050 | Ph A VA | FALSE | #N/A
7103 | 0000E051 | Ph B VA | FALSE | #N/A
7105 | 0000E052 | Ph C VA | FALSE | #N/A
7107 | 0000E060 | Frequency | FALSE | #N/A
7109 | 0000E024 | Angle VTA&VTB | FALSE | #N/A
7111 | 0000E025 | Angle VTA&VTC | FALSE | #N/A
7113 | 0000E026 | Power Factor | FALSE | #N/A
7115 | 00000200 | Im kWh RateA | 57 | #N/A
7117 | 00000201 | Im kWh RateB | 58 | #N/A
7119 | 00000202 | Im kWh RateC | 59 | #N/A
7121 | 00001200 | Im Max kW A | FALSE | #N/A
7123 | 00001201 | Im Max kW B | FALSE | #N/A
7125 | 00001202 | Im Max kW C | FALSE | #N/A
7127 | 00000369 | Im Total kVArh | 63 | #N/A
7129 | 00000360 | Im kVArh A | FALSE | #N/A
7131 | 00000361 | Im kVArh B | FALSE | #N/A
7133 | 00000362 | Im kVArh C | FALSE | #N/A
7135 | 00001300 | Im Max kVArh A | FALSE | #N/A
7137 | 00001301 | Im Max kVArh B | FALSE | #N/A
7139 | 00001302 | Im Max kVArh C | FALSE | #N/A
7141 | 00000340 | Im kVArh-CumA | FALSE | #N/A
7143 | 00000341 | Im kVArh-CumB | FALSE | #N/A
7145 | 00000342 | Im kVArh-CumC | FALSE | #N/A
7147 | 00000249 | Im BT Total kWh | FALSE | #N/A
7149 | 00000240 | Im BT kWh A | FALSE | #N/A
7151 | 00000241 | Im BT kWh B | FALSE | #N/A
7153 | 00000242 | Im BT kWh C | FALSE | #N/A
7155 | 00001220 | Im PV kW A | FALSE | #N/A
7157 | 00001221 | Im PV kW B | FALSE | #N/A
7159 | 00001222 | Im PV kW C | FALSE | #N/A
7161 | 00001240 | Im kW-Cum A | FALSE | #N/A
7163 | 00001241 | Im kW-Cum B | FALSE | #N/A
7165 | 00001242 | Im kW-Cum C | FALSE | #N/A
7167 | 00000149 | Im BT Total kVArh | FALSE | Previous total of kVarh total Reading(Reset)
7169 | 00000329 | Im PV kVAr | FALSE | #N/A
7171 | 00000369 | Im kVAr-Cum | FALSE | #N/A
7173 | 00000269 | Im Total kWh | #N/A | #N/A
7175 | 00001129 | Ex PV KVarh | 89 | Previous kVar demand Total Reading(Reset)
7177 | 00008129 | Ex PV KVarh Time | #N/A | #N/A
7181 | 00001149 | Ex Total kVAr | 90 | Previous Comulative kVarh demand Total Reading(Reset)
7183 | 0000F032 | NB Reset | 91 | PreviousTimes of Reset
7185 | 00008020 | Ex PV kW A Time | #N/A | #N/A
7189 | 00008021 | Ex PV kW B Time | #N/A | #N/A
7193 | 00008022 | Ex PV kW C Time | #N/A | #N/A

## FutureFlex
Check |  | METER |  |  |  | Enos
Inst_kW | 0 | 7001 | 0000E033 | Inst kW | 7000 | 7000 | Used | Inst_kW | 0 | float | AI | 0.001 | 0 | Inst_kW | 7000 | 3 | FLOAT
Inst_kVAr | 1 | 7003 | 0000E043 | Inst kVAr | 7002 | 7002 | Used | Inst_kVAr | 1 | float | AI | 0.001 | 0 | Inst_kVAr | 7002 | 3 | FLOAT
Ex_Total_kWh | 2 | 7005 | 00000069 | Ex Total kWh | 7004 | 7004 | Used | Ex_Total_kWh | 2 | float | AI | 0.001 | 0 | Ex_Total_kWh | 7004 | 3 | FLOAT
Ex_kWh_RateA | 3 | 7007 | 00000000 | Ex kWh RateA | 7006 | 7006 | Used | Ex_kWh_RateA | 3 | float | AI | 0.001 | 0 | Ex_kWh_RateA | 7006 | 3 | FLOAT
Ex_kWh_RateB | 4 | 7009 | 00000001 | Ex kWh RateB | 7008 | 7008 | Used | Ex_kWh_RateB | 4 | float | AI | 0.001 | 0 | Ex_kWh_RateB | 7008 | 3 | FLOAT
Ex_kWh_RateC | 5 | 7011 | 00000002 | Ex kWh RateC | 7010 | 7010 | Used | Ex_kWh_RateC | 5 | float | AI | 0.001 | 0 | Ex_kWh_RateC | 7010 | 3 | FLOAT
FALSE | FALSE | 7013 | 00001000 | Ex Max kW A | 7012 | 7012 |  | Ex_Max_kW_A | 6 | float | AI | 0.001 | 0 | Ex_Max_kW_A | 7012 | 3 | FLOAT
FALSE | FALSE | 7015 | 00001001 | Ex Max kW B | 7014 | 7014 |  | Ex_Max_kW_B | 7 | float | AI | 0.001 | 0 | Ex_Max_kW_B | 7014 | 3 | FLOAT
FALSE | FALSE | 7017 | 00001002 | Ex Max kW C | 7016 | 7016 |  | Ex_Max_kW_C | 8 | float | AI | 0.001 | 0 | Ex_Max_kW_C | 7016 | 3 | FLOAT
FALSE | FALSE | 7019 | 00001040 | Ex kW-Cum A | 7018 | 7018 |  | Ex_kW_Cum_A | 9 | float | AI | 0.001 | 0 | Ex_kW_Cum_A | 7018 | 3 | FLOAT
FALSE | FALSE | 7021 | 00001041 | Ex kW-Cum B | 7020 | 7020 |  | Ex_kW_Cum_B | 10 | float | AI | 0.001 | 0 | Ex_kW_Cum_B | 7020 | 3 | FLOAT
FALSE | FALSE | 7023 | 00001042 | Ex kW-Cum C | 7022 | 7022 |  | Ex_kW_Cum_C | 11 | float | AI | 0.001 | 0 | Ex_kW_Cum_C | 7022 | 3 | FLOAT
Ex_Total_kVArh | 12 | 7025 | 00000169 | Ex Total kVArh | 7024 | 7024 | Used | Ex_Total_kVArh | 12 | float | AI | 0.001 | 0 | Ex_Total_kVArh | 7024 | 3 | FLOAT
FALSE | FALSE | 7027 | 00000160 | Ex kVArh A | 7026 | 7026 |  | Ex_kVArh_RateA | 13 | float | AI | 0.001 | 0 | Ex_kVArh_RateA | 7026 | 3 | FLOAT
FALSE | FALSE | 7029 | 00000161 | Ex kVArh B | 7028 | 7028 |  | Ex_kVArh_RateB | 14 | float | AI | 0.001 | 0 | Ex_kVArh_RateB | 7028 | 3 | FLOAT
FALSE | FALSE | 7031 | 00000162 | Ex kVArh C | 7030 | 7030 |  | Ex_kVArh_RateC | 15 | float | AI | 0.001 | 0 | Ex_kVArh_RateC | 7030 | 3 | FLOAT
FALSE | FALSE | 7033 | 00001100 | Ex Max kVArh A | 7032 | 7032 |  | Ex_Max_kVAr_A | 16 | float | AI | 0.001 | 0 | Ex_Max_kVAr_A | 7032 | 3 | FLOAT
FALSE | FALSE | 7035 | 00001101 | Ex Max kVArh B | 7034 | 7034 |  | Ex_Max_kVAr_B | 17 | float | AI | 0.001 | 0 | Ex_Max_kVAr_B | 7034 | 3 | FLOAT
FALSE | FALSE | 7037 | 00001102 | Ex Max kVArh C | 7036 | 7036 |  | Ex_Max_kVAr_C | 18 | float | AI | 0.001 | 0 | Ex_Max_kVAr_C | 7036 | 3 | FLOAT
FALSE | FALSE | 7039 | 00000140 | Ex kVArh-Cum A | 7038 | 7038 |  | Ex_kVAr_Cum_A | 19 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_A | 7038 | 3 | FLOAT
FALSE | FALSE | 7041 | 00000141 | Ex kVArh-Cum B | 7040 | 7040 |  | Ex_kVAr_Cum_B | 20 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_B | 7040 | 3 | FLOAT
FALSE | FALSE | 7043 | 00000142 | Ex kVArh-Cum C | 7042 | 7042 |  | Ex_kVAr_Cum_C | 21 | float | AI | 0.001 | 0 | Ex_kVAr_Cum_C | 7042 | 3 | FLOAT
FALSE | FALSE | 7045 | 00000049 | Ex BT Total kWh | 7044 | 7044 |  | Ex_BT_Total_kWh | 22 | float | AI | 0.001 | 0 | Ex_BT_Total_kWh | 7044 | 3 | FLOAT
FALSE | FALSE | 7047 | 00000040 | Ex BT kWhA | 7046 | 7046 |  | Ex_BT_kWhA | 23 | float | AI | 0.001 | 0 | Ex_BT_kWhA | 7046 | 3 | FLOAT
FALSE | FALSE | 7049 | 00000041 | Ex BT kWhB | 7048 | 7048 |  | Ex_BT_kWhB | 24 | float | AI | 0.001 | 0 | Ex_BT_kWhB | 7048 | 3 | FLOAT
FALSE | FALSE | 7051 | 00000042 | Ex BT kWhC | 7050 | 7050 |  | Ex_BT_kWhC | 25 | float | AI | 0.001 | 0 | Ex_BT_kWhC | 7050 | 3 | FLOAT
FALSE | FALSE | 7053 | 00001020 | Ex PV kW A | 7052 | 7052 |  | Ex_PV_kW_A | 26 | float | AI | 0.001 | 0 | Ex_PV_kW_A | 7052 | 3 | FLOAT
FALSE | FALSE | 7055 | 00001021 | Ex PV kW B | 7054 | 7054 |  | Ex_PV_kW_B | 27 | float | AI | 0.001 | 0 | Ex_PV_kW_B | 7054 | 3 | FLOAT
FALSE | FALSE | 7057 | 00001022 | Ex PV kW C | 7056 | 7056 |  | Ex_PV_kW_C | 28 | float | AI | 0.001 | 0 | Ex_PV_kW_C | 7056 | 3 | FLOAT
FALSE | FALSE | 7059 | 00001040 | Ex kW-Cum A | 7058 | 7058 |  | Ex_kW_Cum_A2 | 29 | float | AI | 0.001 | 0 | Ex_kW_Cum_A2 | 7058 | 3 | FLOAT
FALSE | FALSE | 7061 | 00001041 | Ex kW-Cum B | 7060 | 7060 |  | Ex_kW_Cum_B2 | 30 | float | AI | 0.001 | 0 | Ex_kW_Cum_B2 | 7060 | 3 | FLOAT
FALSE | FALSE | 7063 | 00001042 | Ex kW-Cum C | 7062 | 7062 |  | Ex_kW_Cum_C2 | 31 | float | AI | 0.001 | 0 | Ex_kW_Cum_C2 | 7062 | 3 | FLOAT
FALSE | FALSE | 7065 | 00000149 | Ex BT Total kVAr | 7064 | 7064 |  | Ex_BT_Total_kVAr | 32 | float | AI | 0.001 | 0 | Ex_BT_Total_kVAr | 7064 | 3 | FLOAT
FALSE | FALSE | 7067 | 00000129 | Ex PV kVAr | 7066 | 7066 |  | Ex_PV_kVAr | 33 | float | AI | 0.001 | 0 | Ex_PV_kVAr | 7066 | 3 | FLOAT
FALSE | FALSE | 7069 | 00000169 | Ex kVAr-Cum | 7068 | 7068 |  | Ex_kVAr_Cum | 34 | float | AI | 0.001 | 0 | Ex_kVAr_Cum | 7068 | 3 | FLOAT
FALSE | FALSE | 7071 | 0000E000 | Ph A Volt | 7070 | 7070 |  | Ph_A_Volt | 35 | float | AI | 1 | 0 | Ph_A_Volt | 7070 | 3 | FLOAT
FALSE | FALSE | 7073 | 0000E001 | Ph B Volt | 7072 | 7072 |  | Ph_B_Volt | 36 | float | AI | 1 | 0 | Ph_B_Volt | 7072 | 3 | FLOAT
FALSE | FALSE | 7075 | 0000E002 | Ph C Volt | 7074 | 7074 |  | Ph_C_Volt | 37 | float | AI | 1 | 0 | Ph_C_Volt | 7074 | 3 | FLOAT
FALSE | FALSE | 7077 | 0000E010 | Ph A Curr | 7076 | 7076 |  | Ph_A_Curr | 38 | float | AI | 1 | 0 | Ph_A_Curr | 7076 | 3 | FLOAT
FALSE | FALSE | 7079 | 0000E011 | Ph B Curr | 7078 | 7078 |  | Ph_B_Curr | 39 | float | AI | 1 | 0 | Ph_B_Curr | 7078 | 3 | FLOAT
FALSE | FALSE | 7081 | 0000E012 | Ph C Curr | 7080 | 7080 |  | Ph_C_Curr | 40 | float | AI | 1 | 0 | Ph_C_Curr | 7080 | 3 | FLOAT
FALSE | FALSE | 7083 | 0000E020 | Ph A angle | 7082 | 7082 |  | Ph_A_angle | 41 | float | AI | 1 | 0 | Ph_A_angle | 7082 | 3 | FLOAT
FALSE | FALSE | 7085 | 0000E021 | Ph B angle | 7084 | 7084 |  | Ph_B_angle | 42 | float | AI | 1 | 0 | Ph_B_angle | 7084 | 3 | FLOAT
FALSE | FALSE | 7087 | 0000E022 | Ph C angle | 7086 | 7086 |  | Ph_C_angle | 43 | float | AI | 1 | 0 | Ph_C_angle | 7086 | 3 | FLOAT
FALSE | FALSE | 7089 | 0000E030 | Ph A Watts | 7088 | 7088 |  | Ph_A_Watts | 44 | float | AI | 0.001 | 0 | Ph_A_Watts | 7088 | 3 | FLOAT
FALSE | FALSE | 7091 | 0000E031 | Ph B Watts | 7090 | 7090 |  | Ph_B_Watts | 45 | float | AI | 0.001 | 0 | Ph_B_Watts | 7090 | 3 | FLOAT
FALSE | FALSE | 7093 | 0000E032 | Ph C Watts | 7092 | 7092 |  | Ph_C_Watts | 46 | float | AI | 0.001 | 0 | Ph_C_Watts | 7092 | 3 | FLOAT
FALSE | FALSE | 7095 | 0000E040 | Ph A vars | 7094 | 7094 |  | Ph_A_vars | 47 | float | AI | 0.001 | 0 | Ph_A_vars | 7094 | 3 | FLOAT
FALSE | FALSE | 7097 | 0000E041 | Ph B vars | 7096 | 7096 |  | Ph_B_vars | 48 | float | AI | 0.001 | 0 | Ph_B_vars | 7096 | 3 | FLOAT
FALSE | FALSE | 7099 | 0000E042 | Ph C vars | 7098 | 7098 |  | Ph_C_vars | 49 | float | AI | 0.001 | 0 | Ph_C_vars | 7098 | 3 | FLOAT
FALSE | FALSE | 7101 | 0000E050 | Ph A VA | 7100 | 7100 |  | Ph_A_VA | 50 | float | AI | 0.001 | 0 | Ph_A_VA | 7100 | 3 | FLOAT
FALSE | FALSE | 7103 | 0000E051 | Ph B VA | 7102 | 7102 |  | Ph_B_VA | 51 | float | AI | 0.001 | 0 | Ph_B_VA | 7102 | 3 | FLOAT
FALSE | FALSE | 7105 | 0000E052 | Ph C VA | 7104 | 7104 |  | Ph_C_VA | 52 | float | AI | 0.001 | 0 | Ph_C_VA | 7104 | 3 | FLOAT
FALSE | FALSE | 7107 | 0000E060 | Frequency | 7106 | 7106 |  | Frequency | 53 | float | AI | 1 | 0 | Frequency | 7106 | 3 | FLOAT
FALSE | FALSE | 7109 | 0000E024 | Angle VTA&VTB | 7108 | 7108 |  | Angle_VT_AB | 54 | float | AI | 1 | 0 | Angle_VT_AB | 7108 | 3 | FLOAT
FALSE | FALSE | 7111 | 0000E025 | Angle VTA&VTC | 7110 | 7110 |  | Angle_VT_AC | 55 | float | AI | 1 | 0 | Angle_VT_AC | 7110 | 3 | FLOAT
FALSE | FALSE | 7113 | 0000E026 | Power Factor | 7112 | 7112 |  | Power_factor | 56 | float | AI | 1 | 0 | Power_factor | 7112 | 3 | FLOAT
Im_kWh_RateA | 57 | 7115 | 00000200 | Im kWh RateA | 7114 | 7114 | Used | Im_kWh_RateA | 57 | float | AI | 0.001 | 0 | Im_kWh_RateA | 7114 | 3 | FLOAT
Im_kWh_RateB | 58 | 7117 | 00000201 | Im kWh RateB | 7116 | 7116 | Used | Im_kWh_RateB | 58 | float | AI | 0.001 | 0 | Im_kWh_RateB | 7116 | 3 | FLOAT
Im_kWh_RateC | 59 | 7119 | 00000202 | Im kWh RateC | 7118 | 7118 | Used | Im_kWh_RateC | 59 | float | AI | 0.001 | 0 | Im_kWh_RateC | 7118 | 3 | FLOAT
FALSE | FALSE | 7121 | 00001200 | Im Max kW A | 7120 | 7120 |  | Im_Max_kW_A | 60 | float | AI | 0.001 | 0 | Im_Max_kW_A | 7120 | 3 | FLOAT
FALSE | FALSE | 7123 | 00001201 | Im Max kW B | 7122 | 7122 |  | Im_Max_kW_B | 61 | float | AI | 0.001 | 0 | Im_Max_kW_B | 7122 | 3 | FLOAT
FALSE | FALSE | 7125 | 00001202 | Im Max kW C | 7124 | 7124 |  | Im_Max_kW_C | 62 | float | AI | 0.001 | 0 | Im_Max_kW_C | 7124 | 3 | FLOAT
Im_Total_kVArh | 63 | 7127 | 00000369 | Im Total kVArh | 7126 | 7126 | Used | Im_Total_kVArh | 63 | float | AI | 0.001 | 0 | Im_Total_kVArh | 7126 | 3 | FLOAT
FALSE | FALSE | 7129 | 00000360 | Im kVArh A | 7128 | 7128 |  | Im_kVArh_RateA | 64 | float | AI | 0.001 | 0 | Im_kVArh_RateA | 7128 | 3 | FLOAT
FALSE | FALSE | 7131 | 00000361 | Im kVArh B | 7130 | 7130 |  | Im_kVArh_RateB | 65 | float | AI | 0.001 | 0 | Im_kVArh_RateB | 7130 | 3 | FLOAT
FALSE | FALSE | 7133 | 00000362 | Im kVArh C | 7132 | 7132 |  | Im_kVArh_RateC | 66 | float | AI | 0.001 | 0 | Im_kVArh_RateC | 7132 | 3 | FLOAT
FALSE | FALSE | 7135 | 00001300 | Im Max kVArh A | 7134 | 7134 |  | Im_Max_kVAr_A | 67 | float | AI | 0.001 | 0 | Im_Max_kVAr_A | 7134 | 3 | FLOAT
FALSE | FALSE | 7137 | 00001301 | Im Max kVArh B | 7136 | 7136 |  | Im_Max_kVAr_B | 68 | float | AI | 0.001 | 0 | Im_Max_kVAr_B | 7136 | 3 | FLOAT
FALSE | FALSE | 7139 | 00001302 | Im Max kVArh C | 7138 | 7138 |  | Im_Max_kVAr_C | 69 | float | AI | 0.001 | 0 | Im_Max_kVAr_C | 7138 | 3 | FLOAT
FALSE | FALSE | 7141 | 00000340 | Im kVArh-CumA | 7140 | 7140 |  | Im_kVAr_Cum_A | 70 | float | AI | 0.001 | 0 | Im_kVAr_Cum_A | 7140 | 3 | FLOAT
FALSE | FALSE | 7143 | 00000341 | Im kVArh-CumB | 7142 | 7142 |  | Im_kVAr_Cum_B | 71 | float | AI | 0.001 | 0 | Im_kVAr_Cum_B | 7142 | 3 | FLOAT
FALSE | FALSE | 7145 | 00000342 | Im kVArh-CumC | 7144 | 7144 |  | Im_kVAr_Cum_C | 72 | float | AI | 0.001 | 0 | Im_kVAr_Cum_C | 7144 | 3 | FLOAT
FALSE | FALSE | 7147 | 00000249 | Im BT Total kWh | 7146 | 7146 |  | Im_BT_Total_kWh | 73 | float | AI | 0.001 | 0 | Im_BT_Total_kWh | 7146 | 3 | FLOAT
FALSE | FALSE | 7149 | 00000240 | Im BT kWh A | 7148 | 7148 |  | Im_BT_kWhA | 74 | float | AI | 0.001 | 0 | Im_BT_kWhA | 7148 | 3 | FLOAT
FALSE | FALSE | 7151 | 00000241 | Im BT kWh B | 7150 | 7150 |  | Im_BT_kWhB | 75 | float | AI | 0.001 | 0 | Im_BT_kWhB | 7150 | 3 | FLOAT
FALSE | FALSE | 7153 | 00000242 | Im BT kWh C | 7152 | 7152 |  | Im_BT_kWhC | 76 | float | AI | 0.001 | 0 | Im_BT_kWhC | 7152 | 3 | FLOAT
FALSE | FALSE | 7155 | 00001220 | Im PV kW A | 7154 | 7154 |  | Im_PV_kW_A | 77 | float | AI | 0.001 | 0 | Im_PV_kW_A | 7154 | 3 | FLOAT
FALSE | FALSE | 7157 | 00001221 | Im PV kW B | 7156 | 7156 |  | Im_PV_kW_B | 78 | float | AI | 0.001 | 0 | Im_PV_kW_B | 7156 | 3 | FLOAT
FALSE | FALSE | 7159 | 00001222 | Im PV kW C | 7158 | 7158 |  | Im_PV_kW_C | 79 | float | AI | 0.001 | 0 | Im_PV_kW_C | 7158 | 3 | FLOAT
FALSE | FALSE | 7161 | 00001240 | Im kW-Cum A | 7160 | 7160 |  | Im_kW_Cum_A | 80 | float | AI | 0.001 | 0 | Im_kW_Cum_A | 7160 | 3 | FLOAT
FALSE | FALSE | 7163 | 00001241 | Im kW-Cum B | 7162 | 7162 |  | Im_kW_Cum_B | 81 | float | AI | 0.001 | 0 | Im_kW_Cum_B | 7162 | 3 | FLOAT
FALSE | FALSE | 7165 | 00001242 | Im kW-Cum C | 7164 | 7164 |  | Im_kW_Cum_C | 82 | float | AI | 0.001 | 0 | Im_kW_Cum_C | 7164 | 3 | FLOAT
FALSE | FALSE | 7167 | 00001349 | Im BT Total kVAr | 7166 | 7166 |  | Im_BT_Total_kVAr | 83 | float | AI | 0.001 | 0 | Im_BT_Total_kVAr | 7166 | 3 | FLOAT
FALSE | FALSE | 7169 | 00000329 | Im PV kVAr | 7168 | 7168 |  | Im_PV_kVAr | 84 | float | AI | 0.001 | 0 | Im_PV_kVAr | 7168 | 3 | FLOAT
FALSE | FALSE | 7171 | 00000369 | Im kVAr-Cum | 7170 | 7170 |  | Im_kVAr_Cum | 85 | float | AI | 0.001 | 0 | Im_kVAr_Cum | 7170 | 3 | FLOAT
Im_total_kWh | 86 | 7173 | 00000269 | Im Total kWh | 7172 | 7172 | Used | Im_total_kWh | 86 | float | AI | 0.001 | 0 | Im_total_kWh | 7172 | 3 | FLOAT
Ex PV KVarh | 88 | 7175 | 00001129 | Ex PV KVarh | 7174 | 7180 | Used | Ex_Total_kVAr | 87 | float | AI | 0.001 | 0 | Ex_Total_kVAr | 7180 | 3 | FLOAT
#N/A | #N/A | 7177 | 00001129 | Ex PV KVarh | 7176 | 7174 | Used | Ex PV KVarh | 88 | float | AI | 0.001 | 0 | Ex PV KVarh | 7174 | 3 | FLOAT
#N/A | #N/A | 7179 | 00008129 | Ex PV KVarh Time | 7178 | 7182 | Used | No_of_Reset | 89 | float | AI | 1 | 0 | No_of_Reset | 7182 | 3 | SHORT
Ex_Total_kVAr | 87 | 7181 | 00008129 | Ex PV KVarh Time | 7180
No_of_Reset | 89 | 7183 | 00001149 | Ex Total kVAr | 7182
#N/A | #N/A | 7185 | 0000F032 | NB Reset | 7184
#N/A | #N/A | 7187 | 00008020 | Ex PV kW A Time | 7186
#N/A | #N/A | 7191 | 00008021 | Ex PV kW B Time | 7190
#N/A | #N/A | 7195 | 00008022 | Ex PV kW C Time | 7194
#N/A | #N/A | 7199 | 0000FC00 | DT of Reset | 7198

## Sheet10
สรุป
VT1 | Modbus_VSPP_CHPP7_MK6E_Exlm_m
VT2 | Modbus_VSPP_CHPP7_MK6E_Exlm_m
KVIS | Modbus_VSPP_CHPP7_MK6E_Exlm_m
TOP1 | Modbus_VSPP_CHPP3_MK6E_Exlm_m
TOP2 | Modbus_VSPP Mk6E_Exlm V1
PTTMRB |  | แก้ ENOS และ Meter
AICA | Modbus_VSPP_CHPP3_MK6E_OR_4 | ใช้กับ VT1&2 KVIS
Suretex | Modbus_VSPP_CHPP3_MK6E_Exlm_m
SUT | Modbus_VSPP_CHPP3_MK6E_Exlm_m
PTIC | Modbus_VSPP_CHPP3_MK6E_Exlm_m
INI | Modbus_VSPP_CHPP3_MK6E_INI_2
RASC | Modbus_VSPP_CHPP3_MK6E_Exlm_m
Enter | Modbus_VSPP_CHPP3_MK6E_Exlm_m
Futureflex | Modbus_VSPP Mk6E_Exlm V1